## 1
1 | Building Summary Small Hotel pre-1980 construction
UWG |  |  | Value | Value | Value
areaFloor |  | Total Floor Area (m2) | 4013.63 | 4013.63 | 4013.63
nFloor |  | Number of Floors | 4 | 4 | 4
glazing |  | Total | 0.1087 | 0.1087 | 0.1087
hCeiling |  | Floor to Floor Height (m) | 2.9 | 2.9 | 2.9 | (average of four floors)
areaWall |  | Gross Dimensions - Total Area (m2) | 1694.66 | 1694.66 | 1694.66
ver2hor |  | Wall to Skin Ratio | 0.6 | 0.6 | 0.62811
areaRoof |  | Gross Dimensions - Total Area (m2) | 1003.3894 | 1003.3894 | 1003.3894
areaWindow |  | Total Area (m2) | 184.21 | 184.21 | 184.21

## 2
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD11PRE | Total | Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.6616 | 184.2302 |  | 254.0541 | 16.0992 | 12.1577 | 4.4926 | 765.5972 | 10 | 0.64427 | 2585.8807 |  | 0.8924
BLD11PST | Total | Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.6616 | 184.2302 |  | 254.0541 | 16.0992 | 12.1577 | 4.4926 | 765.5972 | 10 | 0.64427 | 2585.8807 |  | 0.8924
BLD11PST | Total | Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.6616 | 184.2302 |  | 254.0541 | 26.5146 | 24.3154 | 8.9851 | 765.5972 | 10 | 0.64427 | 2585.8807 |  | 0.23797

## 3
3 |  | Location Summary
Building | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD11PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD11PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD11PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD11PRE | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD11PRE | RvalRoof |  | R-value attic floor (m2·K / W) | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 2.0492 | 1.9802 | 2.0704 | 2.5 | 2.3697 | 2.994 | 2.994 | 2.9326 | 2.994
BLD11PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD11PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD11PRE | HVAC |  | Air Conditioning (kW) | 327.3284 | 335.4719 | 350.4178 | 330.9295 | 288.2535 | 343.8125 | 286.7553 | 320.9209 | 326.6809 | 297.4258 | 305.6705 | 303.3852 | 298.4717 | 289.8795 | 274.3577 | 260.0259
BLD11PRE | HEAT |  | Heating (kW) | 119.4192 | 195.3715 | 153.1418 | 228.8077 | 130.746 | 182.6177 | 153.8575 | 249.6406 | 208.0534 | 199.6262 | 299.3807 | 253.759 | 328.7516 | 310.7575 | 341.7542 | 443.1059
BLD11PRE | COP |  | Air Conditioning (COP) | 3.219 | 3.2176 | 3.2171 | 3.2204 | 3.2327 | 3.2169 | 3.2329 | 3.2249 | 3.2184 | 3.2338 | 3.2297 | 3.226 | 3.233 | 3.2328 | 3.2355 | 3.2355
BLD11PRE | EffHeat |  | CORRIDORFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 17.72 | 18.64 | 20.22 | 19.44 | 17.07 | 20.44 | 17.58 | 18.53 | 20.24 | 18.25 | 17.75 | 19.05 | 17.81 | 18.65 | 17.09 | 17.36
BLD11PST | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD11PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BLD11PST | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD11PST | RvalRoof |  | R-value attic floor (m2·K / W) | 2.381 | 2.6667 | 3.8314 | 2.445 | 1.7606 | 3.663 | 2 | 3.0395 | 2.9851 | 2.7548 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD11PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD11PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD11PST | HVAC |  | Air Conditioning (kW) | 353.8407 | 316.2462 | 332.2653 | 305.7079 | 285.6945 | 309.2 | 260.1402 | 295.1934 | 297.3561 | 267.6579 | 294.7453 | 288.9459 | 283.7106 | 274.0808 | 264.8464 | 257.6261
BLD11PST | HEAT |  | Heating (kW) | 298.184 | 269.9029 | 246.7319 | 288.6891 | 268.3324 | 254.3287 | 269.304 | 299.9559 | 261.4755 | 259.8951 | 350.6096 | 300.508 | 369.7938 | 350.9403 | 372.9051 | 452.5282
BLD11PST | COP |  | Air Conditioning (COP) | 3.0501 | 3.0635 | 3.0453 | 3.071 | 3.0657 | 3.0504 | 3.0485 | 3.0731 | 3.0614 | 3.0639 | 3.0734 | 3.0669 | 3.0812 | 3.0612 | 3.0786 | 3.0365
BLD11PST | EffHeat |  | Heating Efficiency (%) | 0.84768 | 0.87517 | 0.8674 | 0.88078 | 0.84547 | 0.87405 | 0.84919 | 0.88211 | 0.88058 | 0.87555 | 0.89111 | 0.88889 | 0.89341 | 0.8952 | 0.89588 | 0.90229
BLD11PST | Fan |  | Fan Max Flow Rate (m3/s ) | 19.15 | 16.84 | 18.84 | 17.09 | 16.63 | 18.13 | 15.74 | 16.15 | 18.11 | 16.12 | 16.48 | 17.8 | 16.27 | 17.33 | 16.06 | 16.88
BLD11NEW | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD11NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 3.2051
BLD11NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD11NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD11NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD11NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD11NEW | HVAC |  | Air Conditioning (kW) | 276.3634 | 279.8684 | 281.0555 | 262.8575 | 228.8239 | 258.8043 | 238.8149 | 258.3681 | 260.1166 | 227.5111 | 258.1337 | 256.5367 | 252.0397 | 244.8212 | 240.6974 | 205.7895
BLD11NEW | HEAT |  | Heating (kW) | 248.7838 | 286.9997 | 254.3215 | 291.5743 | 232.3817 | 255.473 | 245.0928 | 308.2999 | 270.3047 | 268.9622 | 340.2691 | 299.2654 | 330.22 | 311.7547 | 337.6035 | 392.1863
BLD11NEW | COP |  | Air Conditioning (COP) | 3.4616 | 3.4469 | 3.439 | 3.4641 | 3.4726 | 3.4566 | 3.4463 | 3.4654 | 3.4545 | 3.4619 | 3.4654 | 3.4563 | 3.4682 | 3.4556 | 3.4664 | 3.4564
BLD11NEW | EffHeat |  | Heating Efficiency (%) | 0.83389 | 0.85278 | 0.84461 | 0.8545 | 0.83755 | 0.84827 | 0.84417 | 0.85785 | 0.85425 | 0.85168 | 0.86952 | 0.86689 | 0.88641 | 0.88801 | 0.88933 | 0.89476
BLD11NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 14.25 | 14.72 | 15.61 | 14.51 | 13.11 | 14.96 | 14.25 | 13.84 | 15.51 | 13.42 | 14.07 | 15.42 | 14.15 | 15 | 14.18 | 12.94

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
| Sat |  |  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
| Sun |  |  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
| Sat |  |  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
| Sun |  |  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
| Sat |  |  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
| Sun |  |  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
| Sat |  |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Sun |  |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
| Sat |  |  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
| Sun |  |  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
SchGas | WD | LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
| Sat |  |  |  | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8
| Sun |  |  |  | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8
SchSWH | WD | GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
| Sat |  |  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
| Sun |  |  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8

## BuildingSummary
Building Summary Small Hotel pre-1980 construction
UWG |  |  | Value | Value | Value
Program
|  | Building Name | Small Hotel Reference Building pre-1980 construction | Small Hotel Reference Building post-1980 construction | Small Hotel Reference Building new construction 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Lodging | Lodging | Lodging
Form
areaFloor |  | Total Floor Area (m2) | 4013.63 | 4013.63 | 4013.63
|  | Building Shape | Rectangle | Rectangle | Rectangle
|  | Aspect Ratio | 3 | 3 | 3
nFloor |  | Number of Floors | 4 | 4 | 4
Window Fraction (Window to Wall Ratio)
|  | South | 0.1524 | 0.1524 | 0.1524
|  | East | 0.0313 | 0.0313 | 0.0313
|  | North | 0.1139 | 0.1139 | 0.1139
|  | West | 0.0395 | 0.0395 | 0.0395
glazing |  | Total | 0.1087 | 0.1087 | 0.1087
Skylight/TDD Percentage
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | core zone with four perimeter zones on each floor plus attic | core zone with four perimeter zones on each floor plus attic | core zone with four perimeter zones on each floor
|  | Floor to Ceiling Height (m) | 3.35 1st floor, 2.74 upper floors | 3.35 1st floor, 2.74 upper floors | 3.35 1st floor, 2.74 upper floors
hCeiling |  | Floor to Floor Height (m) | 3.35 1st floor, 2.74 upper floors | 3.35 1st floor, 2.74 upper floors | 3.35 1st floor, 2.74 upper floors
|  | Roof type | Attic | Attic | Built-up flat roof, insulation entirely above deck
Fabric
Exterior walls
|  | Construction Type | Steel frame | Steel frame | Steel frame
areaWall |  | Gross Dimensions - Total Area (m2) | 1694.66 | 1694.66 | 1694.66
|  | Net Dimensions - Total Area (m2) | 1510.43 | 1510.43 | 1510.43
ver2hor |  | Wall to Skin Ratio | 0.6 | 0.6 | 0.62811
Roof
|  | Construction Type | Attic | Attic | IEAD
areaRoof |  | Gross Dimensions - Total Area (m2) | 1003.3894 | 1003.3894 | 1003.3894
|  | Net Dimensions - Total Area (m2) | 1003.3894 | 1003.3894 | 1003.3894
|  | Roof to Skin Ratio | 0.4 | 0.4 | 0.37189
Window Dimensions (m2)
|  | South | 96.83 | 96.83 | 96.83
|  | East | 6.62 | 6.62 | 6.62
|  | North | 72.38 | 72.38 | 72.38
|  | West | 8.38 | 8.38 | 8.38
areaWindow |  | Total Area (m2) | 184.21 | 184.21 | 184.21
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
|  | Foundation Type | Mass Floor | Mass Floor | Mass Floor
|  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
|  | Dimensions - Total Area (m2) | 1661 | 1661 | 1661
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
Dimensions - Total Area (m2)
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 0.95 | 0.95 | 0.25
HVAC
|  | System Type | PTAC | MZ-CAV common areas, PTACs guest rooms | MZ-CAV common areas, PTACs guest rooms
|  | Heating Type | Unit heater, PTAC electric heat | Gas furnace, unit heater, PTAC electric heat | Gas furnace, unit heater, PTAC electric heat
|  | Cooling Type | DX | DX | DX
|  | Fan Control | Constant | Constant | Constant
Service Water Heating
|  | SWH Type | gas water heater | gas water heater | gas water heater
|  | Fuel | gas | gas | gas
|  | Thermal Efficiency (%) | 80 | 78 | 80
|  | Temperature Setpoint (ºC ) | 60 | 60 | 60
|  | Water Consumption (m3 ) | 3470.09 | 3470.09 | 3470.09

## ZoneSummary
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
|  | REARSTAIRSFLR1 | Yes | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 9.9549 | 0 |  |  |  |  | 0 |  | 2.1693 | 43.5369
|  | CORRIDORFLR1 | Yes | 1 | 150.51 | 504.62 | 3.3527 | 32.7 | 9.82 |  | 0 | 9.5035 | 0 |  |  |  | 0.25 | 37.6275 |  | 0.26448 | 39.8066
|  | REARSTORAGEFLR1 | No | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 4.9774 | 0 |  |  |  |  | 0 |  | 2.1693
|  | FRONTLOUNGEFLR1 | Yes | 1 | 163.06 | 546.7 | 3.3528 | 94.0201 | 14.83 | 3.0937 | 52.7076 | 14.1516 | 15.4389 |  |  | 8 |  | 421.6604 |  | 0.7019 | 114.4525
|  | RESTROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 | 32.61 | 1 | 11.8232 | 10.767 |  |  |  |  | 0 | 188.7788 | 0.49608 | 16.1772
|  | MEETINGROOMFLR1 | Yes | 1 | 80.27 | 269.14 | 3.3529 | 32.7 | 4.94 | 1.8581 | 43.2009 | 22.9155 | 12.9047 |  |  | 10 |  | 432.0091 |  | 0.49588 | 39.8042
|  | MECHANICALROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 |  | 0 | 10.3453 | 0 |  |  |  | 0.25 | 8.1525 |  | 0.49608 | 16.1772
|  | GUESTROOM101 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608 | 16.1772
|  | GUESTROOM102 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608 | 16.1772
|  | GUESTROOM103 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.65 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608 | 16.1772
|  | GUESTROOM104 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 21.74 | 1.5 | 20.6895 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49613 | 16.1787
|  | GUESTROOM105 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6895 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49613 | 16.1787
|  | EMPLOYEELOUNGEFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 3.0937 | 10.5409 | 17.7339 | 77.1847 |  |  | 8 |  | 84.3269 |  | 0.49613 | 16.1787
|  | LAUNDRYROOMFLR1 | Yes | 1 | 97.83 | 327.99 | 3.3527 | 39.86 | 4.94 | 9.2903 | 10.5303 | 11.1826 | 21.8747 | 184.3145 | 255.5145 | 13 |  | 136.8942 |  | 0.496 | 48.5239
|  | ELEVATORCOREFLR1 | No | 1 | 15.05 | 50.46 | 3.3528 | 6.13 | 0 |  | 0 | 0 | 128.4161 |  |  |  | 5 | 75.25 |  | 0.49582
|  | EXERCISECENTERFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 3.0937 | 10.5409 | 14.7782 | 11.5041 |  |  | 10 |  | 105.4086 |  | 0.49613 | 16.1787
|  | FRONTOFFICEFLR1 | Yes | 1 | 130.44 | 437.33 | 3.3527 | 53.14 | 6.58 | 13.0064 | 10.0289 | 21.6803 | 12.9047 |  |  | 10 |  | 100.2888 |  | 0.49593 | 64.6889
|  | FRONTSTAIRSFLR1 | Yes | 1 | 20.07 | 67.28 | 3.3523 | 35.77 | 0 |  | 0 | 9.9528 | 0 |  |  |  |  | 0 |  | 2.1699 | 43.5499
|  | FRONTSTORAGEFLR1 | No | 1 | 12.54 | 42.05 | 3.3533 | 5.11 | 0 |  | 0 | 5.7543 | 0 |  |  |  |  | 0 |  | 0.49598
|  | REARSTAIRSFLR2 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 8.7747 | 0 |  |  |  |  | 0 |  | 2.1697 | 43.5452
|  | CORRIDORFLR2 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 0.21816 | 27.3611
|  | REARSTORAGEFLR2 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 2.1693
|  | GUESTROOM201 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.5261 | 49.7651
|  | GUESTROOM202_205 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591 | 64.6921
|  | GUESTROOM206_208 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.49594 | 52.2527
|  | GUESTROOM209_212 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591 | 64.6921
|  | GUESTROOM213 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49591 | 16.1718
|  | GUESTROOM214 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | GUESTROOM215_218 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596 | 64.6926
|  | ELEVATORCOREFLR2 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.49621
|  | GUESTROOM219 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | GUESTROOM220_223 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596 | 64.6926
|  | GUESTROOM224 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | FRONTSTORAGEFLR2 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 0.49579
|  | FRONTSTAIRSFLR2 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 2.1693 | 43.5382
|  | REARSTAIRSFLR3 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 8.7747 | 0 |  |  |  |  | 0 |  | 2.1697 | 43.5452
|  | CORRIDORFLR3 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 0.21816 | 27.3611
|  | REARSTORAGEFLR3 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 2.1693
|  | GUESTROOM301 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.5261 | 49.7651
|  | GUESTROOM302_305 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591 | 64.6921
|  | GUESTROOM306_308 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.49594 | 52.2527
|  | GUESTROOM309_312 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591 | 64.6921
|  | GUESTROOM313 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49591 | 16.1718
|  | GUESTROOM314 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | GUESTROOM315_318 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596 | 64.6926
|  | ELEVATORCOREFLR3 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.49621
|  | GUESTROOM319 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | GUESTROOM320_323 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596 | 64.6926
|  | GUESTROOM324 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | FRONTSTORAGEFLR3 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 0.49579
|  | FRONTSTAIRSFLR3 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 2.1693 | 43.5382
|  | REARSTAIRSFLR4 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 4.3874 | 0 |  |  |  |  | 0 |  | 3.6574 | 73.4035
|  | CORRIDORFLR4 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 1.706 | 213.9639
|  | REARSTORAGEFLR4 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 3.6567
|  | GUESTROOM401 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 3.0138 | 98.2804
|  | GUESTROOM402_405 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838 | 258.7831
|  | GUESTROOM406_408 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 1.9838 | 209.0108
|  | GUESTROOM409_412 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838 | 258.7831
|  | GUESTROOM413 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9837 | 64.6871
|  | GUESTROOM414 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839 | 64.6943
|  | GUESTROOM415_418 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838 | 258.7701
|  | ELEVATORCOREFLR4 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 1.9838
|  | GUESTROOM419 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839 | 64.6943
|  | GUESTROOM420_423 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838 | 258.7701
|  | GUESTROOM424 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839 | 64.6943
|  | FRONTSTORAGEFLR4 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 1.9832
|  | FRONTSTAIRSFLR4 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 3.6573 | 73.4019
|  | ATTIC | No | 1 | 1092.62 | 1582.44 | 1.4483 | 0 | 0 | [8 empty] | 0 |  | 1
BLD11PRE | Total | Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.6616 | 184.2302 |  | 254.0541 | 16.0992 | 12.1577 | 4.4926 | 765.5972 | 10 | 0.64427 | 2585.8807 |  | 0.8924
|  | REARSTAIRSFLR1 | Yes | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 9.9549 | 0 |  |  |  |  | 0 |  | 2.1693 | 43.5369
|  | CORRIDORFLR1 | Yes | 1 | 150.51 | 504.62 | 3.3527 | 32.7 | 9.82 |  | 0 | 9.5035 | 0 |  |  |  | 0.25 | 37.6275 |  | 0.26448 | 39.8066
|  | REARSTORAGEFLR1 | No | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 4.9774 | 0 |  |  |  |  | 0 |  | 2.1693
|  | FRONTLOUNGEFLR1 | Yes | 1 | 163.06 | 546.7 | 3.3528 | 94.0201 | 14.83 | 3.0937 | 52.7076 | 14.1516 | 15.4389 |  |  | 8 |  | 421.6604 |  | 0.7019 | 114.4525
|  | RESTROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 | 32.61 | 1 | 11.8232 | 10.767 |  |  |  |  | 0 | 188.7788 | 0.49608 | 16.1772
|  | MEETINGROOMFLR1 | Yes | 1 | 80.27 | 269.14 | 3.3529 | 32.7 | 4.94 | 1.8581 | 43.2009 | 22.9155 | 12.9047 |  |  | 10 |  | 432.0091 |  | 0.49588 | 39.8042
|  | MECHANICALROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 |  | 0 | 10.3453 | 0 |  |  |  | 0.25 | 8.1525 |  | 0.49608 | 16.1772
|  | GUESTROOM101 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608 | 16.1772
|  | GUESTROOM102 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608 | 16.1772
|  | GUESTROOM103 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.65 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608 | 16.1772
|  | GUESTROOM104 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 21.74 | 1.5 | 20.6895 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49613 | 16.1787
|  | GUESTROOM105 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6895 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49613 | 16.1787
|  | EMPLOYEELOUNGEFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 3.0937 | 10.5409 | 17.7339 | 77.1847 |  |  | 8 |  | 84.3269 |  | 0.49613 | 16.1787
|  | LAUNDRYROOMFLR1 | Yes | 1 | 97.83 | 327.99 | 3.3527 | 39.86 | 4.94 | 9.2903 | 10.5303 | 11.1826 | 21.8747 | 184.3145 | 255.5145 | 13 |  | 136.8942 |  | 0.496 | 48.5239
|  | ELEVATORCOREFLR1 | No | 1 | 15.05 | 50.46 | 3.3528 | 6.13 | 0 |  | 0 | 0 | 128.4161 |  |  |  | 5 | 75.25 |  | 0.49582
|  | EXERCISECENTERFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 3.0937 | 10.5409 | 14.7782 | 11.5041 |  |  | 10 |  | 105.4086 |  | 0.49613 | 16.1787
|  | FRONTOFFICEFLR1 | Yes | 1 | 130.44 | 437.33 | 3.3527 | 53.14 | 6.58 | 13.0064 | 10.0289 | 21.6803 | 12.9047 |  |  | 10 |  | 100.2888 |  | 0.49593 | 64.6889
|  | FRONTSTAIRSFLR1 | Yes | 1 | 20.07 | 67.28 | 3.3523 | 35.77 | 0 |  | 0 | 9.9528 | 0 |  |  |  |  | 0 |  | 2.1699 | 43.5499
|  | FRONTSTORAGEFLR1 | No | 1 | 12.54 | 42.05 | 3.3533 | 5.11 | 0 |  | 0 | 5.7543 | 0 |  |  |  |  | 0 |  | 0.49598
|  | REARSTAIRSFLR2 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 8.7747 | 0 |  |  |  |  | 0 |  | 2.1697 | 43.5452
|  | CORRIDORFLR2 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 0.21816 | 27.3611
|  | REARSTORAGEFLR2 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 2.1693
|  | GUESTROOM201 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.5261 | 49.7651
|  | GUESTROOM202_205 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591 | 64.6921
|  | GUESTROOM206_208 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.49594 | 52.2527
|  | GUESTROOM209_212 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591 | 64.6921
|  | GUESTROOM213 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49591 | 16.1718
|  | GUESTROOM214 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | GUESTROOM215_218 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596 | 64.6926
|  | ELEVATORCOREFLR2 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.49621
|  | GUESTROOM219 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | GUESTROOM220_223 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596 | 64.6926
|  | GUESTROOM224 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | FRONTSTORAGEFLR2 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 0.49579
|  | FRONTSTAIRSFLR2 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 2.1693 | 43.5382
|  | REARSTAIRSFLR3 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 8.7747 | 0 |  |  |  |  | 0 |  | 2.1697 | 43.5452
|  | CORRIDORFLR3 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 0.21816 | 27.3611
|  | REARSTORAGEFLR3 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 2.1693
|  | GUESTROOM301 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.5261 | 49.7651
|  | GUESTROOM302_305 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591 | 64.6921
|  | GUESTROOM306_308 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.49594 | 52.2527
|  | GUESTROOM309_312 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591 | 64.6921
|  | GUESTROOM313 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49591 | 16.1718
|  | GUESTROOM314 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | GUESTROOM315_318 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596 | 64.6926
|  | ELEVATORCOREFLR3 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.49621
|  | GUESTROOM319 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | GUESTROOM320_323 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596 | 64.6926
|  | GUESTROOM324 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597 | 16.1736
|  | FRONTSTORAGEFLR3 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 0.49579
|  | FRONTSTAIRSFLR3 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 2.1693 | 43.5382
|  | REARSTAIRSFLR4 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 4.3874 | 0 |  |  |  |  | 0 |  | 3.6574 | 73.4035
|  | CORRIDORFLR4 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 1.706 | 213.9639
|  | REARSTORAGEFLR4 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 3.6567
|  | GUESTROOM401 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 3.0138 | 98.2804
|  | GUESTROOM402_405 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838 | 258.7831
|  | GUESTROOM406_408 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 1.9838 | 209.0108
|  | GUESTROOM409_412 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838 | 258.7831
|  | GUESTROOM413 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9837 | 64.6871
|  | GUESTROOM414 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839 | 64.6943
|  | GUESTROOM415_418 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838 | 258.7701
|  | ELEVATORCOREFLR4 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 1.9838
|  | GUESTROOM419 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839 | 64.6943
|  | GUESTROOM420_423 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838 | 258.7701
|  | GUESTROOM424 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839 | 64.6943
|  | FRONTSTORAGEFLR4 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 1.9832
|  | FRONTSTAIRSFLR4 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 3.6573 | 73.4019
|  | ATTIC | No | 1 | 1092.62 | 1582.44 | 1.4483 | 0 | 0 | [8 empty] | 0 |  | 1
BLD11PST | Total | Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.6616 | 184.2302 |  | 254.0541 | 16.0992 | 12.1577 | 4.4926 | 765.5972 | 10 | 0.64427 | 2585.8807 |  | 0.8924
|  | REARSTAIRSFLR1 | Yes | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57847 | 11.6098
|  | CORRIDORFLR1 | Yes | 1 | 150.51 | 504.62 | 3.3527 | 32.7 | 9.82 |  | 0 | 5.3819 | 0 |  |  |  | 0.25 | 37.6275 |  | 0.070528 | 10.6151
|  | REARSTORAGEFLR1 | No | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.57847
|  | FRONTLOUNGEFLR1 | Yes | 1 | 163.06 | 546.7 | 3.3528 | 94.0201 | 14.83 | 3.0937 | 52.7076 | 11.8403 | 15.4389 |  |  | 8 |  | 421.6604 |  | 0.18717 | 30.5207
|  | RESTROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 | 32.61 | 1 | 9.6875 | 10.767 |  |  |  |  | 0 | 188.7788 | 0.13229 | 4.3139
|  | MEETINGROOMFLR1 | Yes | 1 | 80.27 | 269.14 | 3.3529 | 32.7 | 4.94 | 1.8581 | 43.2009 | 13.9931 | 12.9047 |  |  | 10 |  | 432.0091 |  | 0.13223 | 10.6145
|  | MECHANICALROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 |  | 0 | 16.1458 | 0 |  |  |  | 0.25 | 8.1525 |  | 0.13229 | 4.3139
|  | GUESTROOM101 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13229 | 4.3139
|  | GUESTROOM102 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13229 | 4.3139
|  | GUESTROOM103 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13229 | 4.3139
|  | GUESTROOM104 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.1323 | 4.3143
|  | GUESTROOM105 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.1323 | 4.3143
|  | EMPLOYEELOUNGEFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 3.0937 | 10.5409 | 12.9167 | 77.1847 |  |  | 8 |  | 84.3269 |  | 0.1323 | 4.3143
|  | LAUNDRYROOMFLR1 | Yes | 1 | 97.83 | 327.99 | 3.3527 | 39.86 | 4.94 | 9.2903 | 10.5303 | 6.4583 | 21.8747 | 184.3145 | 255.5145 | 13 |  | 136.8942 |  | 0.13227 | 12.9397
|  | ELEVATORCOREFLR1 | No | 1 | 15.05 | 50.46 | 3.3528 | 6.13 | 0 |  | 0 | 0 | 128.4161 |  |  |  | 5 | 75.25 |  | 0.13222
|  | EXERCISECENTERFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 3.0937 | 10.5409 | 9.6875 | 11.5041 |  |  | 10 |  | 105.4086 |  | 0.1323 | 4.3143
|  | FRONTOFFICEFLR1 | Yes | 1 | 130.44 | 437.33 | 3.3527 | 53.14 | 6.58 | 13.0064 | 10.0289 | 11.8403 | 12.9047 |  |  | 10 |  | 100.2888 |  | 0.13225 | 17.2504
|  | FRONTSTAIRSFLR1 | Yes | 1 | 20.07 | 67.28 | 3.3523 | 35.77 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57864 | 11.6133
|  | FRONTSTORAGEFLR1 | No | 1 | 12.54 | 42.05 | 3.3533 | 5.11 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.13226
|  | REARSTAIRSFLR2 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57858 | 11.6121
|  | CORRIDORFLR2 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.3819 | 0 |  |  |  | 0.25 | 31.355 |  | 0.058175 | 7.2963
|  | REARSTORAGEFLR2 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.57847
|  | GUESTROOM201 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.40695 | 13.2707
|  | GUESTROOM202_205 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13224 | 17.2512
|  | GUESTROOM206_208 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 11.8403 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.13225 | 13.9341
|  | GUESTROOM209_212 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13224 | 17.2512
|  | GUESTROOM213 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13224 | 4.3125
|  | GUESTROOM214 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226 | 4.313
|  | GUESTROOM215_218 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13226 | 17.2514
|  | ELEVATORCOREFLR2 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.13232
|  | GUESTROOM219 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226 | 4.313
|  | GUESTROOM220_223 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13226 | 17.2514
|  | GUESTROOM224 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226 | 4.313
|  | FRONTSTORAGEFLR2 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.13221
|  | FRONTSTAIRSFLR2 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57849 | 11.6102
|  | REARSTAIRSFLR3 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57858 | 11.6121
|  | CORRIDORFLR3 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.3819 | 0 |  |  |  | 0.25 | 31.355 |  | 0.058175 | 7.2963
|  | REARSTORAGEFLR3 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.57847
|  | GUESTROOM301 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.40695 | 13.2707
|  | GUESTROOM302_305 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13224 | 17.2512
|  | GUESTROOM306_308 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 11.8403 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.13225 | 13.9341
|  | GUESTROOM309_312 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13224 | 17.2512
|  | GUESTROOM313 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13224 | 4.3125
|  | GUESTROOM314 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226 | 4.313
|  | GUESTROOM315_318 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13226 | 17.2514
|  | ELEVATORCOREFLR3 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.13232
|  | GUESTROOM319 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226 | 4.313
|  | GUESTROOM320_323 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13226 | 17.2514
|  | GUESTROOM324 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226 | 4.313
|  | FRONTSTORAGEFLR3 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.13221
|  | FRONTSTAIRSFLR3 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57849 | 11.6102
|  | REARSTAIRSFLR4 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.9753 | 19.5743
|  | CORRIDORFLR4 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.3819 | 0 |  |  |  | 0.25 | 31.355 |  | 0.45493 | 57.057
|  | REARSTORAGEFLR4 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.97512
|  | GUESTROOM401 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.80368 | 26.2081
|  | GUESTROOM402_405 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.52901 | 69.0088
|  | GUESTROOM406_408 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 11.8403 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.52901 | 55.7362
|  | GUESTROOM409_412 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.52901 | 69.0088
|  | GUESTROOM413 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.52898 | 17.2499
|  | GUESTROOM414 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.52903 | 17.2518
|  | GUESTROOM415_418 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.52902 | 69.0054
|  | ELEVATORCOREFLR4 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.52903
|  | GUESTROOM419 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.52903 | 17.2518
|  | GUESTROOM420_423 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.52902 | 69.0054
|  | GUESTROOM424 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.52903 | 17.2518
|  | FRONTSTORAGEFLR4 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.52884
|  | FRONTSTAIRSFLR4 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.97528 | 19.5739
BLD11PST | Total | Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.6616 | 184.2302 |  | 254.0541 | 26.5146 | 24.3154 | 8.9851 | 765.5972 | 10 | 0.64427 | 2585.8807 |  | 0.23797

## LocationSummary
3 |  | Location Summary
Building | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD11PRE |  | Program
BLD11PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD11PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD11PRE
BLD11PRE |  | Fabric
BLD11PRE |  |  | Exterior walls
BLD11PRE | TypeWall |  | Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
BLD11PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD11PRE |  |  | Roof
BLD11PRE | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD11PRE | RvalRoof |  | R-value attic floor (m2·K / W) | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 2.0492 | 1.9802 | 2.0704 | 2.5 | 2.3697 | 2.994 | 2.994 | 2.9326 | 2.994
BLD11PRE |  |  | Window
BLD11PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD11PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD11PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD11PRE |  |  | Skylights/TDD
BLD11PRE |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD11PRE |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD11PRE |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD11PRE |  |  | Foundation
BLD11PRE |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD11PRE |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD11PRE |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD11PRE |  | HVAC
BLD11PRE |  |  | HVAC Sizing
BLD11PRE | HVAC |  | Air Conditioning (kW) | 327.3284 | 335.4719 | 350.4178 | 330.9295 | 288.2535 | 343.8125 | 286.7553 | 320.9209 | 326.6809 | 297.4258 | 305.6705 | 303.3852 | 298.4717 | 289.8795 | 274.3577 | 260.0259
BLD11PRE |  |  | CORRIDORFLR1 PTAC DXCOIL | 10.3264 | 10.383 | 10.4105 | 10.6061 | 9.2966 | 10.0868 | 8.0209 | 9.9477 | 10.5683 | 8.7762 | 9.3829 | 9.8597 | 9.3947 | 9.3987 | 8.4228 | 7.2015
BLD11PRE |  |  | CORRIDORFLR2 PTAC DXCOIL | 5.8807 | 5.9477 | 6.5338 | 6.0652 | 5.3265 | 6.5374 | 5.125 | 5.7194 | 6.2551 | 5.4277 | 5.3395 | 5.6749 | 5.2892 | 5.4429 | 4.9639 | 4.6262
BLD11PRE |  |  | CORRIDORFLR3 PTAC DXCOIL | 5.5806 | 5.6507 | 6.2322 | 5.6803 | 4.8921 | 6.2009 | 4.74 | 5.3261 | 5.7731 | 5.0382 | 4.9665 | 5.2032 | 4.9074 | 5.0126 | 4.602 | 4.321
BLD11PRE |  |  | CORRIDORFLR4 PTAC DXCOIL | 7.0569 | 7.3907 | 8.4179 | 7.491 | 6.0509 | 8.1218 | 5.6692 | 6.6831 | 7.1457 | 6.004 | 5.9323 | 6.0903 | 5.4985 | 5.4784 | 5.0686 | 4.6142
BLD11PRE |  |  | EMPLOYEELOUNGEFLR1 PTAC DXCOIL | 7.8002 | 7.69 | 7.1093 | 7.1783 | 5.6732 | 6.3282 | 5.0843 | 7.0771 | 6.5475 | 5.3312 | 7.5533 | 6.344 | 7.2631 | 6.0088 | 6.1271 | 5.0248
BLD11PRE |  |  | EXERCISECENTERFLR1 PTAC DXCOIL | 3.9425 | 3.9194 | 3.9871 | 4.0368 | 3.1734 | 3.9795 | 1.9905 | 3.7086 | 3.0094 | 2.4811 | 3.5879 | 2.8931 | 3.6249 | 2.455 | 3.1098 | 1.9652
BLD11PRE |  |  | FRONTLOUNGEFLR1 PTAC DXCOIL | 22.5281 | 24.1166 | 26.1654 | 25.36 | 19.8554 | 23.8905 | 17.8153 | 25.0463 | 18.3019 | 18.7079 | 22.2867 | 16.9851 | 22.4304 | 15.6762 | 19.6683 | 14.5728
BLD11PRE |  |  | FRONTOFFICEFLR1 PTAC DXCOIL | 11.0552 | 10.815 | 9.9582 | 10.0079 | 7.2674 | 8.6744 | 5.8929 | 9.6788 | 8.4907 | 6.6426 | 9.8239 | 7.7248 | 9.3865 | 7.3354 | 7.3712 | 5.4021
BLD11PRE |  |  | GUESTROOM101 PTAC DXCOIL | 2.3981 | 2.5563 | 2.5429 | 2.4996 | 2.3039 | 2.3662 | 2.4287 | 2.5163 | 2.3273 | 2.4271 | 2.3096 | 2.1294 | 2.2554 | 2.1352 | 1.8795 | 1.9222
BLD11PRE |  |  | GUESTROOM102 PTAC DXCOIL | 2.4567 | 2.6173 | 2.6131 | 2.5619 | 2.3781 | 2.4513 | 2.5076 | 2.5793 | 2.4074 | 2.5108 | 2.364 | 2.1971 | 2.3104 | 2.2053 | 1.945 | 1.9946
BLD11PRE |  |  | GUESTROOM103 PTAC DXCOIL | 2.6286 | 2.795 | 2.8474 | 2.7335 | 2.4834 | 2.6732 | 2.5245 | 2.7027 | 2.4607 | 2.577 | 2.4742 | 2.2104 | 2.4119 | 2.2308 | 1.9745 | 1.9851
BLD11PRE |  |  | GUESTROOM104 PTAC DXCOIL | 2.5901 | 2.5508 | 2.4434 | 2.3783 | 1.8075 | 2.3631 | 1.4507 | 2.252 | 2.1417 | 1.6902 | 2.237 | 1.8953 | 2.1406 | 1.8118 | 1.6426 | 1.5116
BLD11PRE |  |  | GUESTROOM105 PTAC DXCOIL | 2.5362 | 2.4933 | 2.3268 | 2.3294 | 1.8712 | 2.2705 | 1.5862 | 2.2398 | 2.2627 | 1.7685 | 2.2326 | 2.0561 | 2.1464 | 1.9501 | 1.7336 | 1.4574
BLD11PRE |  |  | GUESTROOM201 PTAC DXCOIL | 4.1068 | 4.2297 | 4.5362 | 4.096 | 3.6986 | 4.5594 | 3.8653 | 3.7935 | 3.9964 | 3.7104 | 3.5847 | 3.6449 | 3.372 | 3.4488 | 3.0703 | 2.8915
BLD11PRE |  |  | GUESTROOM202_205 PTAC DXCOIL | 10.0189 | 10.7961 | 11.3711 | 10.6608 | 10.1176 | 11.1935 | 11.4346 | 10.8062 | 11.0294 | 11.3451 | 10.0687 | 10.2737 | 9.8947 | 10.2922 | 9.3053 | 10.0356
BLD11PRE |  |  | GUESTROOM206_208 PTAC DXCOIL | 8.0175 | 8.6689 | 9.1863 | 8.6002 | 8.3449 | 9.1717 | 9.5569 | 8.766 | 9.0511 | 9.4815 | 8.0571 | 8.317 | 7.9486 | 8.3905 | 7.587 | 8.319
BLD11PRE |  |  | GUESTROOM209_212 PTAC DXCOIL | 9.8536 | 10.6209 | 11.1714 | 10.4821 | 9.9012 | 10.9432 | 11.1906 | 10.6251 | 10.7917 | 11.0929 | 9.9072 | 10.0581 | 9.7339 | 10.0784 | 9.107 | 9.8104
BLD11PRE |  |  | GUESTROOM213 PTAC DXCOIL | 2.7352 | 2.9464 | 3.1773 | 2.9101 | 2.719 | 3.1471 | 2.9764 | 2.9081 | 2.9132 | 3.0099 | 2.7046 | 2.6745 | 2.649 | 2.6963 | 2.4539 | 2.6102
BLD11PRE |  |  | GUESTROOM214 PTAC DXCOIL | 2.7927 | 2.7742 | 2.9874 | 2.7056 | 2.1459 | 2.9544 | 1.9746 | 2.5304 | 2.7026 | 2.1855 | 2.4051 | 2.4361 | 2.4387 | 2.3492 | 2.1473 | 1.9522
BLD11PRE |  |  | GUESTROOM215_218 PTAC DXCOIL | 10.4472 | 10.3361 | 10.502 | 9.884 | 8.3526 | 10.6249 | 7.995 | 9.5996 | 10.5919 | 8.54 | 9.6904 | 9.8857 | 9.3687 | 9.4529 | 8.5716 | 7.9791
BLD11PRE |  |  | GUESTROOM219 PTAC DXCOIL | 3.0051 | 2.9782 | 3.1677 | 2.9982 | 2.5756 | 3.2028 | 2.4699 | 2.8332 | 3.2309 | 2.6311 | 2.837 | 3.0572 | 2.7504 | 2.9207 | 2.6528 | 2.51
BLD11PRE |  |  | GUESTROOM220_223 PTAC DXCOIL | 9.9821 | 9.8711 | 9.8783 | 9.3704 | 7.7568 | 9.9709 | 7.3813 | 9.1375 | 9.8541 | 7.9218 | 9.1733 | 9.1348 | 8.8784 | 8.7399 | 7.9223 | 7.349
BLD11PRE |  |  | GUESTROOM224 PTAC DXCOIL | 2.7415 | 2.7118 | 2.8568 | 2.633 | 2.1138 | 2.843 | 1.9649 | 2.4806 | 2.6823 | 2.1474 | 2.3636 | 2.4393 | 2.2967 | 2.3327 | 2.1331 | 1.967
BLD11PRE |  |  | GUESTROOM301 PTAC DXCOIL | 4.0948 | 4.2084 | 4.5272 | 4.0646 | 3.6326 | 4.5266 | 3.7946 | 3.744 | 3.9432 | 3.6623 | 3.5468 | 3.5993 | 3.3423 | 3.4106 | 3.041 | 2.8822
BLD11PRE |  |  | GUESTROOM302_305 PTAC DXCOIL | 10.0034 | 10.5676 | 11.4142 | 10.6543 | 10.0432 | 11.2295 | 11.4273 | 10.7832 | 11.0258 | 11.3483 | 10.0943 | 10.3265 | 9.9199 | 10.3607 | 9.3802 | 10.1603
BLD11PRE |  |  | GUESTROOM306_308 PTAC DXCOIL | 8.0903 | 8.5473 | 9.3266 | 8.689 | 8.4029 | 9.3308 | 9.7084 | 8.8442 | 9.1629 | 9.6417 | 8.1614 | 8.4607 | 8.0543 | 8.5541 | 7.7492 | 8.5557
BLD11PRE |  |  | GUESTROOM309_312 PTAC DXCOIL | 9.9872 | 10.5507 | 11.3938 | 10.6378 | 10.0262 | 11.203 | 11.4079 | 10.7681 | 11.0034 | 11.3292 | 10.0805 | 10.3038 | 9.9073 | 10.3421 | 9.3644 | 10.1432
BLD11PRE |  |  | GUESTROOM313 PTAC DXCOIL | 2.7448 | 2.9029 | 3.2205 | 2.9314 | 2.7242 | 3.1949 | 3.0088 | 2.9277 | 2.9404 | 3.0497 | 2.7338 | 2.71 | 2.6774 | 2.7418 | 2.5021 | 2.6821
BLD11PRE |  |  | GUESTROOM314 PTAC DXCOIL | 2.8228 | 2.8079 | 3.0653 | 2.7539 | 2.173 | 3.033 | 2.0183 | 2.5671 | 2.7509 | 2.2326 | 2.4454 | 2.4805 | 2.4754 | 2.3983 | 2.2029 | 2.0261
BLD11PRE |  |  | GUESTROOM315_318 PTAC DXCOIL | 10.194 | 10.0968 | 10.2652 | 9.5942 | 8.0075 | 10.3776 | 7.6932 | 9.3596 | 10.1993 | 8.2348 | 9.417 | 9.4777 | 9.1208 | 9.0883 | 8.2679 | 7.7328
BLD11PRE |  |  | GUESTROOM319 PTAC DXCOIL | 2.6666 | 2.6426 | 2.7399 | 2.5455 | 2.1185 | 2.7622 | 2.0284 | 2.4339 | 2.6951 | 2.1776 | 2.4597 | 2.4989 | 2.3826 | 2.3982 | 2.1837 | 2.0376
BLD11PRE |  |  | GUESTROOM320_323 PTAC DXCOIL | 10.0908 | 9.9938 | 10.1249 | 9.4935 | 7.888 | 10.2342 | 7.5767 | 9.2606 | 10.046 | 8.1124 | 9.3143 | 9.3281 | 9.0188 | 8.9455 | 8.1378 | 7.607
BLD11PRE |  |  | GUESTROOM324 PTAC DXCOIL | 2.7516 | 2.731 | 2.9196 | 2.6615 | 2.1203 | 2.9019 | 1.9869 | 2.5013 | 2.7004 | 2.1738 | 2.3874 | 2.4558 | 2.3262 | 2.3527 | 2.1663 | 2.014
BLD11PRE |  |  | GUESTROOM401 PTAC DXCOIL | 4.3471 | 4.4827 | 4.946 | 4.3943 | 3.7375 | 4.8704 | 3.8156 | 3.8823 | 4.1782 | 3.6772 | 3.6396 | 3.7305 | 3.3329 | 3.4021 | 3.0633 | 3.3365
BLD11PRE |  |  | GUESTROOM402_405 PTAC DXCOIL | 11.1926 | 11.5678 | 12.0985 | 11.0628 | 9.8632 | 11.9787 | 11.5373 | 10.7683 | 11.2838 | 11.4322 | 10.2316 | 10.4514 | 9.7762 | 9.9655 | 9.1126 | 10.0349
BLD11PRE |  |  | GUESTROOM406_408 PTAC DXCOIL | 9.0634 | 9.3507 | 9.9388 | 9.0618 | 8.1456 | 9.8405 | 9.7684 | 8.761 | 9.2677 | 9.6715 | 8.2852 | 8.5526 | 7.9323 | 8.1873 | 7.4869 | 8.4746
BLD11PRE |  |  | GUESTROOM409_412 PTAC DXCOIL | 11.192 | 11.5417 | 12.0699 | 11.0722 | 9.8525 | 11.9413 | 11.5323 | 10.7828 | 11.2518 | 11.4293 | 10.2468 | 10.4246 | 9.7703 | 9.9565 | 9.1054 | 10.0349
BLD11PRE |  |  | GUESTROOM413 PTAC DXCOIL | 3.0484 | 3.1578 | 3.4821 | 3.0949 | 2.664 | 3.3941 | 3.0425 | 2.9205 | 3.0144 | 3.0728 | 2.7682 | 2.7528 | 2.639 | 2.6533 | 2.4363 | 2.6545
BLD11PRE |  |  | GUESTROOM414 PTAC DXCOIL | 3.0985 | 3.1488 | 3.58 | 3.1659 | 2.5066 | 3.5015 | 2.2855 | 2.9121 | 3.1034 | 2.5097 | 2.713 | 2.7407 | 2.5949 | 2.5476 | 2.3702 | 2.1486
BLD11PRE |  |  | GUESTROOM415_418 PTAC DXCOIL | 11.1869 | 11.2922 | 12.0615 | 11.0119 | 9.1779 | 11.9828 | 8.5847 | 10.2824 | 11.3666 | 9.1658 | 9.6578 | 10.26 | 9.1548 | 9.4447 | 8.7259 | 8.1294
BLD11PRE |  |  | GUESTROOM419 PTAC DXCOIL | 2.904 | 2.9256 | 3.1954 | 2.9 | 2.3891 | 3.1618 | 2.2208 | 2.6741 | 2.9568 | 2.3777 | 2.4805 | 2.6481 | 2.3737 | 2.432 | 2.2485 | 2.0806
BLD11PRE |  |  | GUESTROOM420_423 PTAC DXCOIL | 11.1166 | 11.2216 | 11.9629 | 10.9196 | 9.0964 | 11.8823 | 8.5096 | 10.2147 | 11.2649 | 9.0848 | 9.5918 | 10.1618 | 9.0683 | 9.352 | 8.6409 | 8.0491
BLD11PRE |  |  | GUESTROOM424 PTAC DXCOIL | 3.0405 | 3.0684 | 3.4494 | 3.0882 | 2.4547 | 3.3823 | 2.2491 | 2.8353 | 3.0517 | 2.4501 | 2.6399 | 2.7112 | 2.5285 | 2.5124 | 2.3364 | 2.144
BLD11PRE |  |  | LAUNDRYROOMFLR1 PTAC DXCOIL | 27.9282 | 27.6523 | 27.2934 | 27.0372 | 25.4091 | 27.4894 | 24.1873 | 26.2794 | 30.24 | 25.1107 | 26.0891 | 29.9808 | 26.1958 | 28.3656 | 25.9211 | 24.3898
BLD11PRE |  |  | MECHANICALROOMFLR1 PTAC DXCOIL | 1.3242 | 1.4373 | 1.381 | 1.3829 | 1.2039 | 1.2375 | 1.2006 | 1.355 | 1.1052 | 1.1764 | 1.2835 | 1.048 | 1.232 | 1.0626 | 0.96483 | 1.1817
BLD11PRE |  |  | MEETINGROOMFLR1 PTAC DXCOIL | 12.3347 | 12.9707 | 13.7126 | 13.6256 | 12.7625 | 13.9755 | 9.7912 | 13.3718 | 11.8331 | 11.1302 | 12.4611 | 11.4006 | 12.6029 | 9.8861 | 12.0254 | 8.1116
BLD11PRE |  |  | RESTROOMFLR1 PTAC DXCOIL | 1.6239 | 1.7462 | 1.8267 | 1.8182 | 1.7485 | 1.826 | 1.7345 | 1.7342 | 1.7607 | 1.727 | 1.6599 | 1.696 | 1.6545 | 1.6767 | 1.4648 | 1.3918
BLD11PRE | HEAT |  | Heating (kW) | 119.4192 | 195.3715 | 153.1418 | 228.8077 | 130.746 | 182.6177 | 153.8575 | 249.6406 | 208.0534 | 199.6262 | 299.3807 | 253.759 | 328.7516 | 310.7575 | 341.7542 | 443.1059
BLD11PRE |  |  | CORRIDORFLR1 PTAC HEAT COIL | 1.8478 | 1.9515 | 1.6465 | 2.5962 | 1.8413 | 1.9228 | 1.6994 | 3.0398 | 2.4439 | 2.0267 | 3.9178 | 3.2114 | 4.5912 | 4.3754 | 4.891 | 6.9593
BLD11PRE |  |  | CORRIDORFLR2 PTAC HEAT COIL | 1.5398 | 1.6346 | 1.3721 | 2.1558 | 1.2812 | 1.529 | 1.4162 | 2.3876 | 1.9055 | 1.6944 | 3.0048 | 2.4746 | 3.4108 | 3.2134 | 3.5745 | 4.7914
BLD11PRE |  |  | CORRIDORFLR3 PTAC HEAT COIL | 1.2319 | 2.0773 | 1.4499 | 2.5922 | 1.2812 | 1.9183 | 1.4398 | 2.8124 | 2.3225 | 2.1003 | 3.4368 | 2.9001 | 3.8315 | 3.6337 | 4.0032 | 5.2453
BLD11PRE |  |  | CORRIDORFLR4 PTAC HEAT COIL | 1.9219 | 3.8189 | 2.8833 | 4.5699 | 2.2473 | 3.5907 | 2.8344 | 4.7791 | 4.2527 | 3.6783 | 5.5089 | 5.0226 | 5.8198 | 5.7355 | 6.1401 | 8.0024
BLD11PRE |  |  | EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | 3.4574 | 4.5642 | 3.8508 | 4.9236 | 3.5958 | 4.1628 | 3.9746 | 5.4808 | 4.3548 | 4.7399 | 6.4028 | 5.1984 | 6.9195 | 6.3053 | 7.0826 | 8.7707
BLD11PRE |  |  | EXERCISECENTERFLR1 PTAC HEAT COIL | 4.3217 | 5.7052 | 4.8135 | 6.1545 | 4.4948 | 5.2035 | 4.9682 | 6.851 | 5.4435 | 5.9249 | 8.0034 | 6.498 | 8.6494 | 7.8817 | 8.8533 | 10.9634
BLD11PRE |  |  | FRONTLOUNGEFLR1 PTAC HEAT COIL | 16.6395 | 21.9664 | 18.533 | 23.6961 | 17.3058 | 20.0346 | 19.1286 | 26.378 | 20.9588 | 22.812 | 30.815 | 25.0188 | 33.3019 | 30.7566 | 34.3081 | 44.9394
BLD11PRE |  |  | FRONTOFFICEFLR1 PTAC HEAT COIL | 3.9288 | 5.9224 | 4.7587 | 7.2113 | 4.0861 | 5.9287 | 4.6389 | 8.0221 | 6.7731 | 6.3216 | 9.8122 | 8.3616 | 10.9368 | 10.3752 | 11.3998 | 14.8785
BLD11PRE |  |  | FRONTSTAIRSFLR1 UNIT HEATER COIL | 0.1392 | 1.3463 | 0.81589 | 1.8542 | 0.42135 | 1.2745 | 0.77823 | 2.1164 | 1.6722 | 1.4229 | 2.9754 | 2.4394 | 3.4524 | 3.2744 | 3.6473 | 5.1584
BLD11PRE |  |  | FRONTSTAIRSFLR2 UNIT HEATER COIL | 0.35115 | 1.2993 | 0.79855 | 1.7072 | 0.49073 | 1.1764 | 0.78229 | 1.9043 | 1.524 | 1.3173 | 2.6109 | 2.1596 | 2.9996 | 2.8474 | 3.1542 | 4.3795
BLD11PRE |  |  | FRONTSTAIRSFLR3 UNIT HEATER COIL | 0.39517 | 1.3402 | 0.83218 | 1.7428 | 0.52367 | 1.2095 | 0.81877 | 1.9393 | 1.5574 | 1.3541 | 2.647 | 2.1941 | 3.0348 | 2.8815 | 3.1905 | 4.416
BLD11PRE |  |  | FRONTSTAIRSFLR4 UNIT HEATER COIL | 0.49359 | 1.5348 | 0.99272 | 1.9725 | 0.64645 | 1.3968 | 0.97446 | 2.1787 | 1.7889 | 1.5411 | 2.9137 | 2.4642 | 3.2958 | 3.1576 | 3.4745 | 4.7927
BLD11PRE |  |  | FRONTSTORAGEFLR1 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05597 | 0 | 0.10501 | 0.10129 | 0.1252 | 0.28239
BLD11PRE |  |  | FRONTSTORAGEFLR2 UNIT HEATER COIL | 0 | 0 | 0 | 0.03112 | 0 | 0 | 0 | 0.03816 | 0 | 0 | 0.10932 | 0.07358 | 0.14614 | 0.13792 | 0.15937 | 0.27127
BLD11PRE |  |  | FRONTSTORAGEFLR3 UNIT HEATER COIL | 0 | 0 | 0 | 0.05343 | 0 | 0 | 0 | 0.05945 | 0.02627 | 0 | 0.12844 | 0.09224 | 0.16426 | 0.15584 | 0.17799 | 0.29012
BLD11PRE |  |  | FRONTSTORAGEFLR4 UNIT HEATER COIL | 0 | 0.12342 | 0.02802 | 0.1992 | 0 | 0.10475 | 0 | 0.20828 | 0.17116 | 0.10127 | 0.292 | 0.25912 | 0.32339 | 0.3253 | 0.35058 | 0.52128
BLD11PRE |  |  | GUESTROOM101 PTAC HEAT COIL | 0.55632 | 1.1637 | 0.95054 | 1.4295 | 0.73062 | 1.1911 | 0.91477 | 1.5655 | 1.3561 | 1.2371 | 1.8937 | 1.6374 | 2.1135 | 2.0236 | 2.2038 | 2.8757
BLD11PRE |  |  | GUESTROOM102 PTAC HEAT COIL | 0.55632 | 1.1855 | 0.97048 | 1.4526 | 0.74959 | 1.2123 | 0.93476 | 1.5893 | 1.3794 | 1.2593 | 1.9173 | 1.6605 | 2.138 | 2.0482 | 2.2288 | 2.9025
BLD11PRE |  |  | GUESTROOM103 PTAC HEAT COIL | 0.72626 | 1.4302 | 1.2019 | 1.7114 | 0.96531 | 1.4585 | 1.1628 | 1.844 | 1.6321 | 1.4976 | 2.1875 | 1.9286 | 2.4136 | 2.3261 | 2.5053 | 3.1959
BLD11PRE |  |  | GUESTROOM104 PTAC HEAT COIL | 0.71733 | 1.4105 | 1.1879 | 1.6914 | 0.95226 | 1.4458 | 1.1488 | 1.8272 | 1.6113 | 1.4778 | 2.178 | 1.9224 | 2.3999 | 2.3122 | 2.4914 | 3.1825
BLD11PRE |  |  | GUESTROOM105 PTAC HEAT COIL | 0.55632 | 1.1788 | 0.9697 | 1.4469 | 0.74459 | 1.2138 | 0.93311 | 1.5876 | 1.3731 | 1.2537 | 1.9243 | 1.6702 | 2.1419 | 2.052 | 2.2331 | 2.9113
BLD11PRE |  |  | GUESTROOM201 PTAC HEAT COIL | 1.2081 | 2.2033 | 1.6761 | 2.6328 | 1.3575 | 2.0691 | 1.6627 | 2.785 | 2.3826 | 2.1861 | 3.3898 | 2.9292 | 3.7484 | 3.5844 | 3.8832 | 4.9909
BLD11PRE |  |  | GUESTROOM202_205 PTAC HEAT COIL | 2.4048 | 4.4566 | 3.3839 | 5.3422 | 2.7364 | 4.1795 | 3.3721 | 5.8049 | 4.8985 | 4.5759 | 6.9484 | 5.9194 | 7.7165 | 7.3247 | 8.0252 | 10.3172
BLD11PRE |  |  | GUESTROOM206_208 PTAC HEAT COIL | 1.7942 | 3.4478 | 2.5951 | 4.1665 | 2.0725 | 3.2365 | 2.5833 | 4.5453 | 3.8286 | 3.5646 | 5.408 | 4.5972 | 6.0194 | 5.7124 | 6.2709 | 8.0797
BLD11PRE |  |  | GUESTROOM209_212 PTAC HEAT COIL | 2.3446 | 4.3573 | 3.3039 | 5.225 | 2.6695 | 4.0822 | 3.2943 | 5.6901 | 4.787 | 4.4807 | 6.8266 | 5.8011 | 7.5868 | 7.1933 | 7.8925 | 10.1662
BLD11PRE |  |  | GUESTROOM213 PTAC HEAT COIL | 0.81934 | 1.3625 | 1.0815 | 1.5935 | 0.90891 | 1.2913 | 1.0768 | 1.7048 | 1.4759 | 1.3848 | 2.004 | 1.7446 | 2.1998 | 2.1032 | 2.2769 | 2.8609
BLD11PRE |  |  | GUESTROOM214 PTAC HEAT COIL | 0.78385 | 1.3275 | 1.0492 | 1.5628 | 0.87336 | 1.263 | 1.0437 | 1.6745 | 1.4419 | 1.3503 | 1.9751 | 1.7186 | 2.1686 | 2.0705 | 2.2463 | 2.8308
BLD11PRE |  |  | GUESTROOM215_218 PTAC HEAT COIL | 2.2253 | 4.0968 | 3.054 | 4.9989 | 2.3918 | 3.859 | 3.0378 | 5.4725 | 4.5447 | 4.2296 | 6.6298 | 5.6042 | 7.3926 | 6.991 | 7.7061 | 10.0183
BLD11PRE |  |  | GUESTROOM219 PTAC HEAT COIL | 0.55632 | 0.84847 | 0.61963 | 1.0898 | 0.5786 | 0.78888 | 0.63954 | 1.2083 | 0.96446 | 0.87662 | 1.5171 | 1.2479 | 1.7166 | 1.6124 | 1.7985 | 2.418
BLD11PRE |  |  | GUESTROOM220_223 PTAC HEAT COIL | 2.2253 | 4.2213 | 3.1869 | 5.1136 | 2.5341 | 3.9807 | 3.1728 | 5.5863 | 4.6649 | 4.3562 | 6.7313 | 5.7141 | 7.4874 | 7.087 | 7.7977 | 10.0751
BLD11PRE |  |  | GUESTROOM224 PTAC HEAT COIL | 0.70663 | 1.274 | 0.98856 | 1.5096 | 0.80448 | 1.2102 | 0.98207 | 1.6255 | 1.3946 | 1.3009 | 1.9162 | 1.6619 | 2.1058 | 2.0065 | 2.1831 | 2.7572
BLD11PRE |  |  | GUESTROOM301 PTAC HEAT COIL | 1.2709 | 2.2653 | 1.7225 | 2.6991 | 1.403 | 2.1197 | 1.7116 | 2.8477 | 2.4392 | 2.2378 | 3.458 | 2.9933 | 3.8132 | 3.6475 | 3.9495 | 5.0596
BLD11PRE |  |  | GUESTROOM302_305 PTAC HEAT COIL | 2.5831 | 4.5987 | 3.4852 | 5.4801 | 2.8467 | 4.2797 | 3.4859 | 5.94 | 5.0167 | 4.6914 | 7.0837 | 6.0477 | 7.8315 | 7.4374 | 8.1471 | 10.4457
BLD11PRE |  |  | GUESTROOM306_308 PTAC HEAT COIL | 2.055 | 3.6714 | 2.7773 | 4.3907 | 2.2644 | 3.4202 | 2.7776 | 4.7673 | 4.0359 | 3.765 | 5.6284 | 4.8098 | 6.2268 | 5.9181 | 6.4863 | 8.3076
BLD11PRE |  |  | GUESTROOM309_312 PTAC HEAT COIL | 2.5661 | 4.5649 | 3.4596 | 5.4393 | 2.8271 | 4.2468 | 3.4614 | 5.9026 | 4.9806 | 4.6623 | 7.0407 | 6.0061 | 7.7861 | 7.3915 | 8.1014 | 10.3936
BLD11PRE |  |  | GUESTROOM313 PTAC HEAT COIL | 0.87194 | 1.4075 | 1.1148 | 1.6394 | 0.94352 | 1.3258 | 1.1131 | 1.7501 | 1.5166 | 1.4237 | 2.0497 | 1.7879 | 2.2417 | 2.1446 | 2.3208 | 2.9074
BLD11PRE |  |  | GUESTROOM314 PTAC HEAT COIL | 0.84321 | 1.3804 | 1.0903 | 1.6173 | 0.9151 | 1.3039 | 1.0877 | 1.7269 | 1.4903 | 1.3976 | 2.0272 | 1.7683 | 2.2174 | 2.1178 | 2.2974 | 2.8831
BLD11PRE |  |  | GUESTROOM315_318 PTAC HEAT COIL | 2.5131 | 4.5136 | 3.4268 | 5.4079 | 2.78 | 4.219 | 3.4264 | 5.8679 | 4.9325 | 4.619 | 7.0106 | 5.9849 | 7.7511 | 7.3457 | 8.0703 | 10.3643
BLD11PRE |  |  | GUESTROOM319 PTAC HEAT COIL | 0.60096 | 1.1528 | 0.857 | 1.3971 | 0.67851 | 1.0752 | 0.85471 | 1.5131 | 1.2663 | 1.1727 | 1.8264 | 1.554 | 2.0253 | 1.9203 | 2.111 | 2.7342
BLD11PRE |  |  | GUESTROOM320_323 PTAC HEAT COIL | 2.4995 | 4.4882 | 3.4058 | 5.3777 | 2.7632 | 4.1937 | 3.4062 | 5.8381 | 4.9044 | 4.5949 | 6.9759 | 5.9532 | 7.7133 | 7.3081 | 8.0311 | 10.3148
BLD11PRE |  |  | GUESTROOM324 PTAC HEAT COIL | 0.78197 | 1.3365 | 1.0394 | 1.5665 | 0.85757 | 1.2582 | 1.0371 | 1.6799 | 1.4449 | 1.3565 | 1.9697 | 1.7134 | 2.1558 | 2.0549 | 2.2352 | 2.8101
BLD11PRE |  |  | GUESTROOM401 PTAC HEAT COIL | 1.4935 | 2.6572 | 2.0405 | 3.1501 | 1.6619 | 2.4962 | 2.0212 | 3.3022 | 2.8834 | 2.5984 | 3.9448 | 3.4895 | 4.2801 | 4.14 | 4.4542 | 5.7147
BLD11PRE |  |  | GUESTROOM402_405 PTAC HEAT COIL | 3.4961 | 6.1828 | 4.7791 | 7.2858 | 3.9058 | 5.8014 | 4.7438 | 7.7461 | 6.7853 | 6.1295 | 8.999 | 8.0052 | 9.6655 | 9.3782 | 10.1235 | 13.0122
BLD11PRE |  |  | GUESTROOM406_408 PTAC HEAT COIL | 2.8103 | 4.9679 | 3.8382 | 5.8666 | 3.1362 | 4.6657 | 3.8099 | 6.244 | 5.4815 | 4.9431 | 7.1942 | 6.409 | 7.7266 | 7.5039 | 8.1016 | 10.4007
BLD11PRE |  |  | GUESTROOM409_412 PTAC HEAT COIL | 3.4851 | 6.1576 | 4.7609 | 7.2547 | 3.8927 | 5.7771 | 4.7265 | 7.7181 | 6.7585 | 6.1086 | 8.9656 | 7.973 | 9.6301 | 9.3425 | 10.088 | 12.9715
BLD11PRE |  |  | GUESTROOM413 PTAC HEAT COIL | 1.0984 | 1.8008 | 1.4358 | 2.0885 | 1.2064 | 1.7038 | 1.4252 | 2.1995 | 1.9565 | 1.7813 | 2.5271 | 2.2756 | 2.6994 | 2.6288 | 2.8141 | 3.5461
BLD11PRE |  |  | GUESTROOM414 PTAC HEAT COIL | 1.0827 | 1.7939 | 1.4297 | 2.0897 | 1.1935 | 1.7009 | 1.4181 | 2.1995 | 1.9535 | 1.7755 | 2.5298 | 2.2815 | 2.7003 | 2.6278 | 2.8179 | 3.5552
BLD11PRE |  |  | GUESTROOM415_418 PTAC HEAT COIL | 3.4758 | 6.1407 | 4.7646 | 7.2585 | 3.8852 | 5.7803 | 4.7286 | 7.7144 | 6.7448 | 6.102 | 8.9656 | 7.9831 | 9.6263 | 9.3253 | 10.0886 | 12.9672
BLD11PRE |  |  | GUESTROOM419 PTAC HEAT COIL | 0.9316 | 1.6688 | 1.291 | 1.9761 | 1.0468 | 1.5719 | 1.2789 | 2.0927 | 1.8362 | 1.649 | 2.4367 | 2.1788 | 2.6133 | 2.5391 | 2.7399 | 3.5286
BLD11PRE |  |  | GUESTROOM420_423 PTAC HEAT COIL | 3.4395 | 6.0952 | 4.7241 | 7.2083 | 3.8475 | 5.7353 | 4.6886 | 7.6641 | 6.696 | 6.0573 | 8.9116 | 7.9307 | 9.57 | 9.2689 | 10.0312 | 12.9031
BLD11PRE |  |  | GUESTROOM424 PTAC HEAT COIL | 1.043 | 1.7559 | 1.4015 | 2.0416 | 1.1596 | 1.664 | 1.3912 | 2.1548 | 1.9111 | 1.7424 | 2.4734 | 2.2279 | 2.6393 | 2.5655 | 2.7559 | 3.483
BLD11PRE |  |  | LAUNDRYROOMFLR1 PTAC HEAT COIL | 7.0228 | 7.4168 | 6.2575 | 8.0008 | 6.9978 | 6.7646 | 6.4586 | 8.9064 | 7.0766 | 7.7023 | 10.4045 | 8.4474 | 11.2442 | 10.2462 | 11.5093 | 15.0169
BLD11PRE |  |  | MECHANICALROOMFLR1 PTAC HEAT COIL | 0.37283 | 0.91995 | 0.77158 | 1.1346 | 0.58449 | 0.96985 | 0.73217 | 1.2187 | 1.0753 | 0.96177 | 1.5018 | 1.3186 | 1.6692 | 1.6103 | 1.735 | 2.2643
BLD11PRE |  |  | MEETINGROOMFLR1 PTAC HEAT COIL | 16.8654 | 22.2646 | 18.7845 | 24.0178 | 17.5407 | 20.3066 | 19.3883 | 26.7361 | 21.2433 | 23.1216 | 31.2333 | 25.3584 | 33.754 | 30.7581 | 34.5498 | 42.7845
BLD11PRE |  |  | REARSTAIRSFLR1 UNIT HEATER COIL | 0.07041 | 1.2364 | 0.7216 | 1.7236 | 0.34002 | 1.1601 | 0.68481 | 1.9796 | 1.5417 | 1.3053 | 2.8233 | 2.2857 | 3.2989 | 3.1227 | 3.4918 | 4.9976
BLD11PRE |  |  | REARSTAIRSFLR2 UNIT HEATER COIL | 0.24294 | 1.1489 | 0.67212 | 1.5441 | 0.3782 | 1.0282 | 0.65901 | 1.7408 | 1.362 | 1.1701 | 2.4391 | 1.9862 | 2.8269 | 2.6755 | 2.9808 | 4.1996
BLD11PRE |  |  | REARSTAIRSFLR3 UNIT HEATER COIL | 0.27468 | 1.179 | 0.69294 | 1.5752 | 0.40113 | 1.0522 | 0.68193 | 1.7717 | 1.3908 | 1.1971 | 2.4718 | 2.018 | 2.8587 | 2.7068 | 3.0138 | 4.2333
BLD11PRE |  |  | REARSTAIRSFLR4 UNIT HEATER COIL | 0.36446 | 1.3681 | 0.83545 | 1.799 | 0.50767 | 1.2325 | 0.81812 | 2.005 | 1.6165 | 1.3753 | 2.7287 | 2.2792 | 3.1092 | 2.9723 | 3.2863 | 4.5966
BLD11PRE |  |  | REARSTORAGEFLR1 UNIT HEATER COIL | 0 | 0.80169 | 0.47094 | 1.148 | 0.19816 | 0.78855 | 0.4291 | 1.2493 | 1.022 | 0.80336 | 1.7554 | 1.4759 | 2.0321 | 1.9604 | 2.1372 | 2.996
BLD11PRE |  |  | REARSTORAGEFLR2 UNIT HEATER COIL | 0.19133 | 0.83053 | 0.50253 | 1.1079 | 0.29073 | 0.7606 | 0.48364 | 1.1789 | 0.97281 | 0.79849 | 1.6015 | 1.3596 | 1.8268 | 1.7615 | 1.9088 | 2.6018
BLD11PRE |  |  | REARSTORAGEFLR3 UNIT HEATER COIL | 0.21791 | 0.84948 | 0.51681 | 1.1262 | 0.30706 | 0.77432 | 0.49963 | 1.1967 | 0.98885 | 0.81516 | 1.6199 | 1.3769 | 1.8442 | 1.7779 | 1.9263 | 2.616
BLD11PRE |  |  | REARSTORAGEFLR4 UNIT HEATER COIL | 0.22768 | 0.8612 | 0.52532 | 1.1412 | 0.31519 | 0.78579 | 0.50909 | 1.2139 | 1.0051 | 0.83038 | 1.6383 | 1.3946 | 1.8601 | 1.7929 | 1.9445 | 2.6384
BLD11PRE |  |  | RESTROOMFLR1 PTAC HEAT COIL | 0.17815 | 0.64586 | 0.5519 | 0.82784 | 0.38493 | 0.72157 | 0.50645 | 0.86809 | 0.79421 | 0.67175 | 1.0635 | 0.96056 | 1.1832 | 1.1616 | 1.2311 | 1.6138
BLD11PRE |  |  | HVAC Efficiency
BLD11PRE | COP |  | Air Conditioning (COP) | 3.219 | 3.2176 | 3.2171 | 3.2204 | 3.2327 | 3.2169 | 3.2329 | 3.2249 | 3.2184 | 3.2338 | 3.2297 | 3.226 | 3.233 | 3.2328 | 3.2355 | 3.2355
BLD11PRE |  |  | CORRIDORFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | CORRIDORFLR2 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | CORRIDORFLR3 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | CORRIDORFLR4 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | EMPLOYEELOUNGEFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | EXERCISECENTERFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4
BLD11PRE |  |  | FRONTLOUNGEFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | FRONTOFFICEFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM101 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM102 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM103 PTAC DXCOIL | 3.4 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM104 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM105 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM201 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM202_205 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM206_208 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM209_212 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM213 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM214 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM215_218 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM219 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.4
BLD11PRE |  |  | GUESTROOM220_223 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM224 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM301 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM302_305 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM306_308 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM309_312 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM313 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21
BLD11PRE |  |  | GUESTROOM314 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM315_318 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM319 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM320_323 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM324 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM401 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM402_405 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM406_408 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM409_412 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM413 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21
BLD11PRE |  |  | GUESTROOM414 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM415_418 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM419 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | GUESTROOM420_423 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | GUESTROOM424 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.4 | 3.21 | 3.4 | 3.21 | 3.21 | 3.4 | 3.4 | 3.21 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | LAUNDRYROOMFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | MECHANICALROOMFLR1 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | MEETINGROOMFLR1 PTAC DXCOIL | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21
BLD11PRE |  |  | RESTROOMFLR1 PTAC DXCOIL | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4
BLD11PRE |  |  | Heating Efficiency (%)
BLD11PRE | EffHeat |  | CORRIDORFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | CORRIDORFLR2 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | CORRIDORFLR3 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | CORRIDORFLR4 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | EXERCISECENTERFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | FRONTLOUNGEFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | FRONTOFFICEFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | FRONTSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | FRONTSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | FRONTSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | FRONTSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | FRONTSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | FRONTSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | FRONTSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | FRONTSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM101 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM102 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM103 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM104 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM105 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM201 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM202_205 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM206_208 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM209_212 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM213 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM214 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM215_218 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM219 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM220_223 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM224 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM301 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM302_305 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM306_308 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM309_312 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM313 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM314 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM315_318 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM319 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM320_323 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM324 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM401 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM402_405 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM406_408 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM409_412 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM413 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM414 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM415_418 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM419 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM420_423 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | GUESTROOM424 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | LAUNDRYROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | MECHANICALROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | MEETINGROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | REARSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | REARSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | REARSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | REARSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | REARSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | REARSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | REARSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | REARSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | RESTROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PRE |  |  | HVAC Control - Economizer
BLD11PRE |  |  | All Systems | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 17.72 | 18.64 | 20.22 | 19.44 | 17.07 | 20.44 | 17.58 | 18.53 | 20.24 | 18.25 | 17.75 | 19.05 | 17.81 | 18.65 | 17.09 | 17.36
BLD11PRE |  |  | CORRIDORFLR1 PTACFAN | 0.62 | 0.63 | 0.63 | 0.64 | 0.56 | 0.61 | 0.48 | 0.6 | 0.64 | 0.53 | 0.57 | 0.6 | 0.57 | 0.57 | 0.51 | 0.44
BLD11PRE |  |  | CORRIDORFLR2 PTACFAN | 0.35 | 0.36 | 0.39 | 0.37 | 0.32 | 0.39 | 0.31 | 0.35 | 0.38 | 0.33 | 0.32 | 0.34 | 0.32 | 0.33 | 0.3 | 0.28
BLD11PRE |  |  | CORRIDORFLR3 PTACFAN | 0.33 | 0.34 | 0.38 | 0.34 | 0.3 | 0.37 | 0.29 | 0.32 | 0.35 | 0.3 | 0.3 | 0.31 | 0.3 | 0.3 | 0.28 | 0.26
BLD11PRE |  |  | CORRIDORFLR4 PTACFAN | 0.43 | 0.45 | 0.51 | 0.45 | 0.37 | 0.49 | 0.34 | 0.4 | 0.43 | 0.36 | 0.36 | 0.37 | 0.33 | 0.33 | 0.31 | 0.28
BLD11PRE |  |  | EMPLOYEELOUNGEFLR1 PTACFAN | 0.35 | 0.35 | 0.36 | 0.36 | 0.33 | 0.37 | 0.31 | 0.34 | 0.4 | 0.32 | 0.34 | 0.38 | 0.34 | 0.36 | 0.33 | 0.3
BLD11PRE |  |  | EXERCISECENTERFLR1 PTACFAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.14 | 0.16 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.16 | 0.15 | 0.15 | 0.13 | 0.12
BLD11PRE |  |  | FRONTLOUNGEFLR1 PTACFAN | 0.91 | 0.97 | 1.05 | 1.02 | 1 | 1.07 | 1.08 | 1.01 | 1.05 | 1.08 | 0.9 | 0.96 | 0.9 | 0.95 | 0.84 | 0.88
BLD11PRE |  |  | FRONTOFFICEFLR1 PTACFAN | 0.53 | 0.53 | 0.53 | 0.52 | 0.43 | 0.52 | 0.36 | 0.48 | 0.51 | 0.4 | 0.45 | 0.47 | 0.45 | 0.44 | 0.39 | 0.33
BLD11PRE |  |  | FRONTSTAIRSFLR1 UNIT HEATERFAN | 0 | 0.05 | 0.03 | 0.06 | 0.01 | 0.05 | 0.03 | 0.07 | 0.07 | 0.05 | 0.1 | 0.1 | 0.12 | 0.13 | 0.13 | 0.17
BLD11PRE |  |  | FRONTSTAIRSFLR2 UNIT HEATERFAN | 0.01 | 0.04 | 0.03 | 0.06 | 0.02 | 0.04 | 0.03 | 0.06 | 0.06 | 0.04 | 0.09 | 0.09 | 0.1 | 0.11 | 0.11 | 0.15
BLD11PRE |  |  | FRONTSTAIRSFLR3 UNIT HEATERFAN | 0.01 | 0.04 | 0.03 | 0.06 | 0.02 | 0.04 | 0.03 | 0.07 | 0.06 | 0.05 | 0.09 | 0.09 | 0.1 | 0.11 | 0.11 | 0.15
BLD11PRE |  |  | FRONTSTAIRSFLR4 UNIT HEATERFAN | 0.02 | 0.05 | 0.03 | 0.07 | 0.02 | 0.05 | 0.03 | 0.07 | 0.07 | 0.05 | 0.1 | 0.1 | 0.11 | 0.12 | 0.12 | 0.16
BLD11PRE |  |  | FRONTSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01
BLD11PRE |  |  | FRONTSTORAGEFLR2 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01
BLD11PRE |  |  | FRONTSTORAGEFLR3 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01
BLD11PRE |  |  | FRONTSTORAGEFLR4 UNIT HEATERFAN | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02
BLD11PRE |  |  | GUESTROOM101 PTACFAN | 0.12 | 0.13 | 0.14 | 0.14 | 0.14 | 0.14 | 0.15 | 0.14 | 0.14 | 0.15 | 0.12 | 0.13 | 0.12 | 0.13 | 0.11 | 0.12
BLD11PRE |  |  | GUESTROOM102 PTACFAN | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.15 | 0.15 | 0.14 | 0.15 | 0.15 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12
BLD11PRE |  |  | GUESTROOM103 PTACFAN | 0.14 | 0.15 | 0.16 | 0.16 | 0.15 | 0.16 | 0.15 | 0.15 | 0.15 | 0.16 | 0.14 | 0.13 | 0.14 | 0.13 | 0.12 | 0.12
BLD11PRE |  |  | GUESTROOM104 PTACFAN | 0.14 | 0.14 | 0.15 | 0.14 | 0.11 | 0.14 | 0.09 | 0.13 | 0.13 | 0.1 | 0.12 | 0.11 | 0.12 | 0.11 | 0.1 | 0.09
BLD11PRE |  |  | GUESTROOM105 PTACFAN | 0.14 | 0.14 | 0.14 | 0.14 | 0.11 | 0.14 | 0.1 | 0.13 | 0.14 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.1 | 0.09
BLD11PRE |  |  | GUESTROOM201 PTACFAN | 0.23 | 0.24 | 0.27 | 0.25 | 0.22 | 0.28 | 0.23 | 0.22 | 0.24 | 0.22 | 0.21 | 0.22 | 0.2 | 0.21 | 0.19 | 0.17
BLD11PRE |  |  | GUESTROOM202_205 PTACFAN | 0.53 | 0.58 | 0.66 | 0.62 | 0.61 | 0.68 | 0.69 | 0.62 | 0.67 | 0.69 | 0.57 | 0.62 | 0.57 | 0.62 | 0.56 | 0.61
BLD11PRE |  |  | GUESTROOM206_208 PTACFAN | 0.43 | 0.47 | 0.54 | 0.51 | 0.5 | 0.55 | 0.58 | 0.51 | 0.55 | 0.57 | 0.46 | 0.5 | 0.47 | 0.51 | 0.46 | 0.5
BLD11PRE |  |  | GUESTROOM209_212 PTACFAN | 0.52 | 0.57 | 0.64 | 0.61 | 0.6 | 0.66 | 0.68 | 0.6 | 0.65 | 0.67 | 0.55 | 0.61 | 0.56 | 0.61 | 0.55 | 0.59
BLD11PRE |  |  | GUESTROOM213 PTACFAN | 0.15 | 0.16 | 0.19 | 0.17 | 0.16 | 0.19 | 0.18 | 0.17 | 0.18 | 0.18 | 0.16 | 0.16 | 0.16 | 0.16 | 0.15 | 0.16
BLD11PRE |  |  | GUESTROOM214 PTACFAN | 0.16 | 0.16 | 0.18 | 0.16 | 0.13 | 0.18 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
BLD11PRE |  |  | GUESTROOM215_218 PTACFAN | 0.59 | 0.59 | 0.63 | 0.6 | 0.5 | 0.64 | 0.48 | 0.56 | 0.64 | 0.52 | 0.54 | 0.6 | 0.54 | 0.57 | 0.52 | 0.48
BLD11PRE |  |  | GUESTROOM219 PTACFAN | 0.18 | 0.18 | 0.19 | 0.18 | 0.16 | 0.19 | 0.15 | 0.17 | 0.2 | 0.16 | 0.17 | 0.18 | 0.17 | 0.18 | 0.16 | 0.15
BLD11PRE |  |  | GUESTROOM220_223 PTACFAN | 0.55 | 0.55 | 0.6 | 0.56 | 0.47 | 0.6 | 0.45 | 0.53 | 0.6 | 0.48 | 0.5 | 0.55 | 0.5 | 0.53 | 0.48 | 0.44
BLD11PRE |  |  | GUESTROOM224 PTACFAN | 0.16 | 0.16 | 0.17 | 0.16 | 0.13 | 0.17 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
BLD11PRE |  |  | GUESTROOM301 PTACFAN | 0.23 | 0.24 | 0.27 | 0.25 | 0.22 | 0.27 | 0.23 | 0.22 | 0.24 | 0.22 | 0.21 | 0.22 | 0.2 | 0.21 | 0.18 | 0.17
BLD11PRE |  |  | GUESTROOM302_305 PTACFAN | 0.54 | 0.57 | 0.66 | 0.62 | 0.61 | 0.68 | 0.69 | 0.61 | 0.67 | 0.69 | 0.57 | 0.62 | 0.58 | 0.63 | 0.57 | 0.61
BLD11PRE |  |  | GUESTROOM306_308 PTACFAN | 0.44 | 0.47 | 0.55 | 0.51 | 0.51 | 0.56 | 0.59 | 0.51 | 0.55 | 0.58 | 0.47 | 0.51 | 0.48 | 0.52 | 0.47 | 0.52
BLD11PRE |  |  | GUESTROOM309_312 PTACFAN | 0.53 | 0.56 | 0.66 | 0.62 | 0.61 | 0.68 | 0.69 | 0.61 | 0.66 | 0.68 | 0.57 | 0.62 | 0.58 | 0.62 | 0.57 | 0.61
BLD11PRE |  |  | GUESTROOM313 PTACFAN | 0.15 | 0.16 | 0.19 | 0.18 | 0.16 | 0.19 | 0.18 | 0.17 | 0.18 | 0.18 | 0.16 | 0.16 | 0.16 | 0.17 | 0.15 | 0.16
BLD11PRE |  |  | GUESTROOM314 PTACFAN | 0.16 | 0.16 | 0.19 | 0.17 | 0.13 | 0.18 | 0.12 | 0.16 | 0.17 | 0.13 | 0.15 | 0.15 | 0.15 | 0.14 | 0.13 | 0.12
BLD11PRE |  |  | GUESTROOM315_318 PTACFAN | 0.57 | 0.57 | 0.62 | 0.58 | 0.48 | 0.63 | 0.46 | 0.54 | 0.62 | 0.5 | 0.52 | 0.57 | 0.52 | 0.55 | 0.5 | 0.47
BLD11PRE |  |  | GUESTROOM319 PTACFAN | 0.15 | 0.15 | 0.17 | 0.15 | 0.13 | 0.17 | 0.12 | 0.14 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
BLD11PRE |  |  | GUESTROOM320_323 PTACFAN | 0.56 | 0.56 | 0.61 | 0.57 | 0.48 | 0.62 | 0.46 | 0.54 | 0.61 | 0.49 | 0.51 | 0.56 | 0.51 | 0.54 | 0.49 | 0.46
BLD11PRE |  |  | GUESTROOM324 PTACFAN | 0.16 | 0.16 | 0.18 | 0.16 | 0.13 | 0.18 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
BLD11PRE |  |  | GUESTROOM401 PTACFAN | 0.25 | 0.26 | 0.3 | 0.27 | 0.23 | 0.29 | 0.23 | 0.23 | 0.25 | 0.22 | 0.21 | 0.23 | 0.2 | 0.21 | 0.19 | 0.2
BLD11PRE |  |  | GUESTROOM402_405 PTACFAN | 0.63 | 0.65 | 0.73 | 0.67 | 0.6 | 0.72 | 0.7 | 0.62 | 0.68 | 0.69 | 0.59 | 0.63 | 0.57 | 0.6 | 0.55 | 0.61
BLD11PRE |  |  | GUESTROOM406_408 PTACFAN | 0.52 | 0.54 | 0.6 | 0.55 | 0.49 | 0.59 | 0.59 | 0.51 | 0.56 | 0.58 | 0.48 | 0.52 | 0.47 | 0.49 | 0.45 | 0.51
BLD11PRE |  |  | GUESTROOM409_412 PTACFAN | 0.63 | 0.65 | 0.73 | 0.66 | 0.6 | 0.72 | 0.7 | 0.62 | 0.68 | 0.69 | 0.59 | 0.63 | 0.57 | 0.6 | 0.55 | 0.61
BLD11PRE |  |  | GUESTROOM413 PTACFAN | 0.18 | 0.18 | 0.21 | 0.19 | 0.16 | 0.21 | 0.18 | 0.17 | 0.18 | 0.19 | 0.16 | 0.17 | 0.16 | 0.16 | 0.15 | 0.16
BLD11PRE |  |  | GUESTROOM414 PTACFAN | 0.19 | 0.19 | 0.22 | 0.19 | 0.15 | 0.21 | 0.14 | 0.18 | 0.19 | 0.15 | 0.16 | 0.17 | 0.16 | 0.15 | 0.14 | 0.13
BLD11PRE |  |  | GUESTROOM415_418 PTACFAN | 0.64 | 0.66 | 0.73 | 0.67 | 0.55 | 0.72 | 0.52 | 0.62 | 0.69 | 0.55 | 0.57 | 0.62 | 0.55 | 0.57 | 0.53 | 0.49
BLD11PRE |  |  | GUESTROOM419 PTACFAN | 0.17 | 0.17 | 0.19 | 0.18 | 0.14 | 0.19 | 0.13 | 0.16 | 0.18 | 0.14 | 0.15 | 0.16 | 0.14 | 0.15 | 0.14 | 0.13
BLD11PRE |  |  | GUESTROOM420_423 PTACFAN | 0.64 | 0.65 | 0.72 | 0.66 | 0.55 | 0.72 | 0.51 | 0.61 | 0.68 | 0.55 | 0.57 | 0.61 | 0.55 | 0.56 | 0.52 | 0.49
BLD11PRE |  |  | GUESTROOM424 PTACFAN | 0.18 | 0.19 | 0.21 | 0.19 | 0.15 | 0.2 | 0.14 | 0.17 | 0.18 | 0.15 | 0.16 | 0.16 | 0.15 | 0.15 | 0.14 | 0.13
BLD11PRE |  |  | LAUNDRYROOMFLR1 PTACFAN | 1.59 | 1.58 | 1.62 | 1.62 | 1.53 | 1.66 | 1.46 | 1.56 | 1.83 | 1.52 | 1.58 | 1.81 | 1.58 | 1.71 | 1.57 | 1.47
BLD11PRE |  |  | MECHANICALROOMFLR1 PTACFAN | 0.06 | 0.07 | 0.08 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.06 | 0.07 | 0.06 | 0.06 | 0.07
BLD11PRE |  |  | MEETINGROOMFLR1 PTACFAN | 0.5 | 0.52 | 0.55 | 0.55 | 0.54 | 0.56 | 0.56 | 0.54 | 0.58 | 0.57 | 0.5 | 0.55 | 0.51 | 0.54 | 0.48 | 0.49
BLD11PRE |  |  | REARSTAIRSFLR1 UNIT HEATERFAN | 0 | 0.04 | 0.03 | 0.06 | 0.01 | 0.04 | 0.02 | 0.07 | 0.06 | 0.04 | 0.1 | 0.09 | 0.11 | 0.12 | 0.12 | 0.17
BLD11PRE |  |  | REARSTAIRSFLR2 UNIT HEATERFAN | 0.01 | 0.04 | 0.02 | 0.05 | 0.01 | 0.04 | 0.02 | 0.06 | 0.06 | 0.04 | 0.08 | 0.08 | 0.1 | 0.1 | 0.1 | 0.14
BLD11PRE |  |  | REARSTAIRSFLR3 UNIT HEATERFAN | 0.01 | 0.04 | 0.02 | 0.05 | 0.01 | 0.04 | 0.02 | 0.06 | 0.06 | 0.04 | 0.08 | 0.08 | 0.1 | 0.1 | 0.11 | 0.14
BLD11PRE |  |  | REARSTAIRSFLR4 UNIT HEATERFAN | 0.01 | 0.05 | 0.03 | 0.06 | 0.02 | 0.04 | 0.03 | 0.07 | 0.07 | 0.05 | 0.09 | 0.09 | 0.11 | 0.11 | 0.12 | 0.16
BLD11PRE |  |  | REARSTORAGEFLR1 UNIT HEATERFAN | 0 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.01 | 0.04 | 0.04 | 0.03 | 0.06 | 0.06 | 0.07 | 0.08 | 0.08 | 0.1
BLD11PRE |  |  | REARSTORAGEFLR2 UNIT HEATERFAN | 0.01 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.04 | 0.04 | 0.03 | 0.05 | 0.06 | 0.06 | 0.07 | 0.07 | 0.09
BLD11PRE |  |  | REARSTORAGEFLR3 UNIT HEATERFAN | 0.01 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.04 | 0.04 | 0.03 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.09
BLD11PRE |  |  | REARSTORAGEFLR4 UNIT HEATERFAN | 0.01 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.04 | 0.04 | 0.03 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.09
BLD11PRE |  |  | RESTROOMFLR1 PTACFAN | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.1 | 0.1 | 0.11 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.09 | 0.08
BLD11PRE |  | Utility Costs
BLD11PRE |  |  | Electric Utility Rates
BLD11PRE |  |  | Average Annual Rate ($/kWh) | 0.079051 | 0.10802 | 0.087357 | 0.10015 | 0.12324 | 0.094839 | 0.14501 | 0.069942 | 0.037194 | 0.071815 | 0.0963 | 0.0372 | 0.056427 | 0.073085 | 0.056906 | 0.093034
BLD11PRE |  |  | Total Cost ($/m2) | 17.18 | 21.81 | 17.8 | 18.89 | 21.88 | 18.29 | 23.97 | 12.99 | 6.7 | 12 | 17.74 | 6.56 | 10.97 | 13.13 | 11.09 | 22.3
BLD11PRE |  |  | Gas Utility Rates
BLD11PRE |  |  | Average Annual Rate ($/MJ) | 0.01146 | 0.0082004 | 0.0086055 | 0.010915 | 0.0083923 | 0.0081734 | 0.0083919 | 0.01015 | 0.0072406 | 0.0082682 | 0.0090446 | 0.0072473 | 0.0080119 | 0.0089154 | 0.0080171 | 0.0042313
BLD11PRE |  |  | Total Cost ($/m2) | 1.25 | 0.99 | 0.98 | 1.45 | 1.1 | 1 | 1.18 | 1.45 | 1.02 | 1.22 | 1.36 | 1.09 | 1.27 | 1.42 | 1.36 | 0.78
BLD11PRE |  |  | Total Utility Costs
BLD11PRE |  |  | Cost Intensity ($/m2) | 18.43 | 22.8 | 18.78 | 20.35 | 22.97 | 19.29 | 25.16 | 14.44 | 7.72 | 13.22 | 19.1 | 7.65 | 12.24 | 14.55 | 12.45 | 23.08
BLD11PRE |  | Energy - End Uses
BLD11PRE |  |  | Electricity (kWh)
BLD11PRE |  |  | Heating | 19.4444 | 8558.3333 | 2319.4444 | 24283.3333 | 180.5556 | 7261.1111 | 3363.8889 | 46694.4444 | 22663.8889 | 24905.5556 | 66366.6667 | 41027.7778 | 111552.7778 | 73811.1111 | 146513.8889 | 338402.7778
BLD11PRE |  |  | Cooling | 267991.6667 | 204441.6667 | 215361.1111 | 141091.6667 | 122811.1111 | 170752.7778 | 77002.7778 | 110986.1111 | 111102.7778 | 63838.8889 | 87950 | 81388.8889 | 82875 | 63908.3333 | 52597.2222 | 39375
BLD11PRE |  |  | Interior Lighting | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667
BLD11PRE |  |  | Exterior Lighting | 73086.1111 | 72955.5556 | 72936.1111 | 73058.3333 | 73044.4444 | 72972.2222 | 72894.4444 | 72969.4444 | 72955.5556 | 72847.2222 | 72869.4444 | 72880.5556 | 72927.7778 | 72838.8889 | 72819.4444 | 72383.3333
BLD11PRE |  |  | Interior Equipment | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667
BLD11PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Fans | 32991.6667 | 25863.8889 | 28916.6667 | 20247.2222 | 18027.7778 | 24561.1111 | 11850 | 16497.2222 | 17986.1111 | 10658.3333 | 13805.5556 | 14033.3333 | 14525 | 12219.4444 | 11530.5556 | 13441.6667
BLD11PRE |  |  | Pumps | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475
BLD11PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Total End Uses | 872497.2222 | 810230.5556 | 817941.6667 | 757086.1111 | 712472.2222 | 773955.5556 | 663516.6667 | 745555.5556 | 723116.6667 | 670661.1111 | 739397.2222 | 707738.8889 | 780288.8889 | 721186.1111 | 781866.6667 | 962013.8889
BLD11PRE |  |  | Gas (MJ)
BLD11PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Equipment | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480
BLD11PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Water Systems | 247280 | 297060 | 268460 | 344970 | 335670 | 302920 | 376670 | 382630 | 375520 | 402240 | 415710 | 413990 | 444290 | 449480 | 491410 | 548430
BLD11PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Total End Uses | 436750 | 486540 | 457940 | 534450 | 525150 | 492400 | 566150 | 572110 | 565000 | 591710 | 605190 | 603470 | 633770 | 638960 | 680890 | 737910
BLD11PRE |  |  | Purchased Cooling (MJ)
BLD11PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Purchased Heating (MJ)
BLD11PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Total Building (MJ) | 3577740 | 3403370 | 3402530 | 3259950 | 3090040 | 3278640 | 2954810 | 3256110 | 3168220 | 3006090 | 3267030 | 3151330 | 3442810 | 3235230 | 3495610 | 4201160
BLD11PRE |  | Energy - End Use Intensities
BLD11PRE |  |  | Electricity (MJ/m2)
BLD11PRE |  |  | Heating (elec) | 0.017441 | 7.6764 | 2.0804 | 21.781 | 0.16195 | 6.5129 | 3.0172 | 41.8827 | 20.3284 | 22.3391 | 59.5278 | 36.8 | 100.0576 | 66.2051 | 131.416 | 303.5313
BLD11PRE |  |  | Cooling (elec) | 240.3758 | 183.3745 | 193.1687 | 126.5525 | 110.1557 | 153.1571 | 69.0678 | 99.5493 | 99.6539 | 57.2605 | 78.887 | 73.002 | 74.3349 | 57.3227 | 47.1772 | 35.3175
BLD11PRE |  |  | Interior Lighting (elec) | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551
BLD11PRE |  |  | Exterior Lighting (elec) | 65.5548 | 65.4377 | 65.4202 | 65.5299 | 65.5174 | 65.4526 | 65.3829 | 65.4501 | 65.4377 | 65.3405 | 65.3604 | 65.3704 | 65.4128 | 65.333 | 65.3156 | 64.9244
BLD11PRE |  |  | Interior Equipment (elec) | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675
BLD11PRE |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Fans (elec) | 29.592 | 23.1987 | 25.9369 | 18.1608 | 16.1701 | 22.0302 | 10.6289 | 14.7972 | 16.1327 | 9.56 | 12.3829 | 12.5872 | 13.0282 | 10.9603 | 10.3424 | 12.0565
BLD11PRE |  |  | Pumps (elec) | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605
BLD11PRE |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Total End Uses | 782.5887 | 726.7384 | 733.6549 | 679.0704 | 639.0538 | 694.2015 | 595.143 | 668.728 | 648.6014 | 601.5512 | 663.2043 | 634.8082 | 699.8822 | 646.8698 | 701.2973 | 862.8809
BLD11PRE |  |  | Gas (MJ/m2)
BLD11PRE |  |  | Heating (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Equipment (gas) | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096
BLD11PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Water Systems (gas) | 61.6107 | 74.0135 | 66.8877 | 85.9505 | 83.6334 | 75.4736 | 93.8486 | 95.3336 | 93.5621 | 100.2195 | 103.5756 | 103.1471 | 110.6964 | 111.9895 | 122.4365 | 136.6433
BLD11PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Total End Uses | 108.8178 | 121.2231 | 114.0974 | 133.1601 | 130.843 | 122.6832 | 141.0583 | 142.5432 | 140.7717 | 147.4266 | 150.7852 | 150.3567 | 157.906 | 159.1991 | 169.6461 | 183.8529
BLD11PRE |  |  | Purchased Cooling (MJ/m2)
BLD11PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Purchased Heating (MJ/m2)
BLD11PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Total Building (MJ/m2) | 891.4064 | 847.9616 | 847.7523 | 812.228 | 769.8943 | 816.8846 | 736.2013 | 811.2712 | 789.3731 | 748.9778 | 813.992 | 785.1649 | 857.7882 | 806.0689 | 870.9435 | 1046.7337
BLD11PRE |  | Peak Energy Demand
BLD11PRE |  |  | Electricity Peak Demand (kW)
BLD11PRE |  |  | Jan | 150.8302 | 164.0306 | 134.1068 | 173.8353 | 132.1964 | 124.0024 | 124.2109 | 196.3023 | 147.9993 | 126.8311 | 218.1102 | 192.9975 | 246.3319 | 221.4929 | 257.5189 | 360.6813
BLD11PRE |  |  | Feb | 152.9571 | 140.0124 | 134.2299 | 174.3046 | 133.0169 | 128.1243 | 130.555 | 156.9855 | 125.0876 | 124.8087 | 164.692 | 169.5689 | 222.0618 | 207.5689 | 256.6967 | 340.5898
BLD11PRE |  |  | Mar | 156.5244 | 151.3064 | 152.4158 | 139.7791 | 131.4861 | 132.6128 | 126.6074 | 133.596 | 129.006 | 131.2386 | 129.3215 | 132.6347 | 151.8749 | 154.3007 | 210.7534 | 260.537
BLD11PRE |  |  | Apr | 161.321 | 160.2624 | 153.031 | 149.6304 | 138.2609 | 150.1791 | 132.9431 | 137.4228 | 139.3855 | 132.1311 | 129.0872 | 135.7752 | 137.0718 | 128.7854 | 124.4293 | 155.1984
BLD11PRE |  |  | May | 165.0349 | 171.9455 | 175.9861 | 162.1033 | 141.8902 | 159.1021 | 134.5803 | 148.477 | 146.6649 | 137.8168 | 144.254 | 143.6562 | 159.2256 | 135.5349 | 133.2678 | 117.767
BLD11PRE |  |  | Jun | 177.222 | 169.3291 | 197.7642 | 164.8682 | 140.6205 | 190.2383 | 135.8525 | 166.2448 | 154.702 | 139.7398 | 154.4134 | 146.8197 | 158.742 | 148.5208 | 148.8115 | 126.8929
BLD11PRE |  |  | Jul | 171.4215 | 176.8698 | 193.066 | 174.7696 | 143.9488 | 185.8496 | 153.0663 | 173.7972 | 163.6086 | 147.4036 | 163.2821 | 153.9738 | 164.252 | 144.0632 | 154.6821 | 132.6549
BLD11PRE |  |  | Aug | 172.1127 | 183.3364 | 197.5227 | 166.1151 | 145.6293 | 178.7916 | 135.9211 | 174.8876 | 160.3833 | 147.782 | 167.9751 | 150.7923 | 163.5322 | 148.0767 | 155.9559 | 131.4888
BLD11PRE |  |  | Sep | 167.6368 | 168.3272 | 180.8181 | 158.2767 | 144.8721 | 164.8545 | 145.2255 | 151.8909 | 149.0932 | 152.7096 | 147.9577 | 144.2771 | 144.4449 | 145.1105 | 140.3944 | 126.775
BLD11PRE |  |  | Oct | 165.678 | 160.4614 | 156.3209 | 147.8485 | 140.0783 | 146.4975 | 135.0609 | 145.6648 | 140.2385 | 132.9291 | 137.9022 | 137.8396 | 139.3929 | 131.6396 | 134.2956 | 176.145
BLD11PRE |  |  | Nov | 157.5998 | 150.3117 | 138.3384 | 132.9722 | 134.7592 | 130.1613 | 128.1646 | 139.9735 | 128.0794 | 133.3772 | 137.5621 | 129.7379 | 148.6508 | 134.9201 | 193.9415 | 233.8997
BLD11PRE |  |  | Dec | 150.9443 | 149.0058 | 133.4113 | 160.5456 | 132.3041 | 125.5043 | 123.4719 | 167.0195 | 145.7635 | 130.6114 | 199.1447 | 180.7088 | 250.7613 | 232.674 | 246.6438 | 301.9919
BLD11PRE |  |  | Time of Peak Electrical Demand
BLD11PRE |  |  | Jan | 06-JAN-20:00 | 14-JAN-07:15 | 29-JAN-20:15 | 14-JAN-07:15 | 26-JAN-20:15 | 10-JAN-20:45 | 15-JAN-20:15 | 31-JAN-07:15 | 04-JAN-07:15 | 02-JAN-07:00 | 07-JAN-07:15 | 06-JAN-06:15 | 06-JAN-06:15 | 07-JAN-07:15 | 09-JAN-07:15 | 13-JAN-06:15
BLD11PRE |  |  | Feb | 20-FEB-20:15 | 20-FEB-20:15 | 28-FEB-20:15 | 10-FEB-07:15 | 12-FEB-20:15 | 27-FEB-20:15 | 15-FEB-20:15 | 01-FEB-07:15 | 14-FEB-20:15 | 01-FEB-07:15 | 09-FEB-06:15 | 16-FEB-06:45 | 04-FEB-06:15 | 26-FEB-07:15 | 02-FEB-07:15 | 04-FEB-07:15
BLD11PRE |  |  | Mar | 13-MAR-19:15 | 26-MAR-19:15 | 17-MAR-19:15 | 28-MAR-19:15 | 04-MAR-20:00 | 31-MAR-19:00 | 30-MAR-19:30 | 09-MAR-20:00 | 20-MAR-19:15 | 29-MAR-19:00 | 03-MAR-20:00 | 07-MAR-06:15 | 05-MAR-21:00 | 04-MAR-06:15 | 09-MAR-06:15 | 14-MAR-06:00
BLD11PRE |  |  | Apr | 01-APR-19:15 | 30-APR-19:15 | 02-APR-19:15 | 15-APR-19:15 | 11-APR-19:15 | 21-APR-19:15 | 29-APR-19:15 | 05-APR-19:15 | 22-APR-19:15 | 29-APR-19:15 | 28-APR-19:30 | 25-APR-19:30 | 02-APR-19:30 | 30-APR-19:30 | 15-APR-19:15 | 02-APR-06:15
BLD11PRE |  |  | May | 15-MAY-19:15 | 26-MAY-19:15 | 28-MAY-19:30 | 14-MAY-19:30 | 29-MAY-19:15 | 31-MAY-19:15 | 25-MAY-19:15 | 15-MAY-19:15 | 30-MAY-19:15 | 04-MAY-19:30 | 30-MAY-19:15 | 23-MAY-19:15 | 27-MAY-19:45 | 25-MAY-19:00 | 31-MAY-19:00 | 29-MAY-19:00
BLD11PRE |  |  | Jun | 27-JUN-19:15 | 13-JUN-19:30 | 27-JUN-19:45 | 19-JUN-19:00 | 28-JUN-19:15 | 27-JUN-19:15 | 16-JUN-19:30 | 30-JUN-19:45 | 28-JUN-19:30 | 18-JUN-20:15 | 16-JUN-19:30 | 27-JUN-19:30 | 29-JUN-19:00 | 25-JUN-20:30 | 14-JUN-19:00 | 23-JUN-19:00
BLD11PRE |  |  | Jul | 04-JUL-19:15 | 30-JUL-19:15 | 11-JUL-19:45 | 02-JUL-19:00 | 10-JUL-19:15 | 24-JUL-19:15 | 02-JUL-19:30 | 24-JUL-19:30 | 30-JUL-19:15 | 24-JUL-19:00 | 13-JUL-19:30 | 17-JUL-19:30 | 15-JUL-19:00 | 30-JUL-19:00 | 06-JUL-19:00 | 29-JUL-19:15
BLD11PRE |  |  | Aug | 21-AUG-19:15 | 06-AUG-19:15 | 01-AUG-19:30 | 14-AUG-19:30 | 16-AUG-19:15 | 04-AUG-19:15 | 27-AUG-19:15 | 03-AUG-19:15 | 01-AUG-19:15 | 06-AUG-19:45 | 04-AUG-19:15 | 29-AUG-19:15 | 27-AUG-19:15 | 11-AUG-19:45 | 13-AUG-19:30 | 19-AUG-20:00
BLD11PRE |  |  | Sep | 10-SEP-19:15 | 16-SEP-19:15 | 09-SEP-19:15 | 10-SEP-19:15 | 25-SEP-19:15 | 01-SEP-19:00 | 28-SEP-19:00 | 09-SEP-19:15 | 02-SEP-19:15 | 02-SEP-19:15 | 06-SEP-19:15 | 01-SEP-19:15 | 14-SEP-19:15 | 02-SEP-19:15 | 08-SEP-19:15 | 09-SEP-19:45
BLD11PRE |  |  | Oct | 06-OCT-19:15 | 29-OCT-19:15 | 02-OCT-19:15 | 01-OCT-19:15 | 05-OCT-19:15 | 03-OCT-19:15 | 16-OCT-19:15 | 20-OCT-19:15 | 01-OCT-19:15 | 09-OCT-19:15 | 31-OCT-19:15 | 01-OCT-19:15 | 08-OCT-19:15 | 06-OCT-19:15 | 07-OCT-19:15 | 22-OCT-07:15
BLD11PRE |  |  | Nov | 01-NOV-19:15 | 26-NOV-20:00 | 05-NOV-19:15 | 22-NOV-20:00 | 09-NOV-20:30 | 09-NOV-20:30 | 12-NOV-20:30 | 04-NOV-19:15 | 09-NOV-20:00 | 29-NOV-07:15 | 02-NOV-19:00 | 18-NOV-20:00 | 30-NOV-07:15 | 30-NOV-07:15 | 25-NOV-07:15 | 23-NOV-06:15
BLD11PRE |  |  | Dec | 17-DEC-20:15 | 02-DEC-20:15 | 13-DEC-20:15 | 22-DEC-07:15 | 18-DEC-20:15 | 05-DEC-20:15 | 17-DEC-20:15 | 21-DEC-07:15 | 29-DEC-07:15 | 11-DEC-07:15 | 31-DEC-07:15 | 12-DEC-07:15 | 31-DEC-06:15 | 11-DEC-07:15 | 31-DEC-07:15 | 29-DEC-06:15
BLD11PRE |  | Source Energy
BLD11PRE |  |  | Total Source Energy (GJ) | 10895.59 | 11125.22 | 9813.82 | 9752.22 | 8511.81 | 10504.07 | 8011.15 | 10222.73 | 9254.47 | 4852 | 10099.73 | 9112.78 | 10346.76 | 9722.37 | 10417.71 | 13176.52
BLD11PRE |  |  | Total Source Energy (MJ/m2) | 2714.68 | 2771.89 | 2445.15 | 2429.8 | 2120.75 | 2617.13 | 1996.01 | 2547.03 | 2305.78 | 1208.89 | 2516.39 | 2270.48 | 2577.93 | 2422.37 | 2595.61 | 3282.98
BLD11PRE |  | Water Consumption (m3)
BLD11PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Water Systems | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13
BLD11PRE |  |  | Total Building | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13
BLD11PRE |  | Emissions
BLD11PRE |  |  | Carbon Equivalent (kg) | 247157.725 | 279034.6777 | 255174.5904 | 242847.4891 | 92733.3226 | 269914.9529 | 87751.7219 | 211508.8781 | 305580.3579 | 59517.1683 | 405122.9008 | 299991.8913 | 278516.2125 | 275070.5034 | 279905.4116 | 284004.8068
BLD11PRE |  |  | CO2 (kg) | 576824.9099 | 703511.121 | 604532.2318 | 557138.0192 | 249659.6499 | 643920.1292 | 236521.8071 | 480987.2199 | 717728.213 | 146863.3053 | 941079.1197 | 705094.4113 | 648761.4981 | 646268.9039 | 652460.194 | 716548.9385
BLD11PRE |  |  | NOX (kg) | 997.8194 | 914.3959 | 1003.0931 | 1047.3442 | 215.0777 | 1037.2024 | 203.946 | 929.153 | 1234.359 | 214.4263 | 1684.8186 | 1210.4955 | 1153.5942 | 1118.3192 | 1158.0927 | 884.4377
BLD11PRE |  |  | SO2 (kg) | 3734.75 | 3864.9277 | 3289.2322 | 2657.5116 | 2073.3464 | 4257.5036 | 1930.9089 | 2721.7289 | 3157.8598 | 518.5256 | 4983.1152 | 3090.7139 | 1841.7779 | 1925.8241 | 1845.5106 | 4897.23
BLD11PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PRE |  |  | Hg (kg) | 0.0171 | 0.0109 | 0.009 | 0.0098 | 0.001 | 0.008 | 0.0009 | 0.011 | 0.0124 | 0.0021 | 0.0151 | 0.0121 | 0.0135 | 0.0134 | 0.0135 | 0.0166
BLD11PRE |  |  | Water for Electricity (m3) | 462.2119 | 1318.34 | 24296.5 | 4726.94 | 12509.4 | 21232.7 | 11649.9 | 169.2691 | 3283.53 | 6852.01 | 1147.13 | 3213.7 | 1210.57 | 45682.9 | 1213.02 | 982.8697
BLD11PST |  | Program
BLD11PST |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD11PST |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD11PST |  | Fabric
BLD11PST |  |  | Exterior walls
BLD11PST | TypeWall |  | Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
BLD11PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BLD11PST |  |  | Roof
BLD11PST | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD11PST | RvalRoof |  | R-value attic floor (m2·K / W) | 2.381 | 2.6667 | 3.8314 | 2.445 | 1.7606 | 3.663 | 2 | 3.0395 | 2.9851 | 2.7548 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD11PST |  |  | Window
BLD11PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD11PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD11PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD11PST |  |  | Skylights/TDD
BLD11PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD11PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD11PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD11PST |  |  | Foundation
BLD11PST |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD11PST |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD11PST |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD11PST |  | HVAC
BLD11PST |  |  | HVAC Sizing
BLD11PST | HVAC |  | Air Conditioning (kW) | 353.8407 | 316.2462 | 332.2653 | 305.7079 | 285.6945 | 309.2 | 260.1402 | 295.1934 | 297.3561 | 267.6579 | 294.7453 | 288.9459 | 283.7106 | 274.0808 | 264.8464 | 257.6261
BLD11PST |  |  | GUESTROOM101 PTAC DXCOIL | 2.6009 | 2.3637 | 2.45 | 2.2122 | 2.2033 | 2.0616 | 1.9457 | 2.1331 | 1.9748 | 1.9346 | 2.1249 | 1.9236 | 2.0042 | 1.8491 | 1.7041 | 1.761
BLD11PST |  |  | GUESTROOM102 PTAC DXCOIL | 2.6608 | 2.417 | 2.5133 | 2.2639 | 2.2724 | 2.1303 | 2.0122 | 2.183 | 2.0405 | 2.004 | 2.1754 | 1.9869 | 2.0539 | 1.9131 | 1.7534 | 1.842
BLD11PST |  |  | GUESTROOM103 PTAC DXCOIL | 2.9844 | 2.5446 | 2.7586 | 2.3739 | 2.3763 | 2.2909 | 1.9867 | 2.2516 | 2.0383 | 2.0075 | 2.2307 | 1.947 | 2.0816 | 1.8731 | 1.7095 | 1.7126
BLD11PST |  |  | GUESTROOM104 PTAC DXCOIL | 2.9096 | 2.345 | 2.3963 | 2.2636 | 1.7776 | 2.1017 | 1.3569 | 2.1523 | 1.8919 | 1.5463 | 2.1223 | 1.7802 | 2.0031 | 1.6868 | 1.554 | 1.2433
BLD11PST |  |  | GUESTROOM105 PTAC DXCOIL | 2.7483 | 2.3199 | 2.2545 | 2.2435 | 1.8445 | 2.0528 | 1.5172 | 2.174 | 2.0493 | 1.6627 | 2.1634 | 1.9832 | 2.0618 | 1.8702 | 1.6937 | 1.4705
BLD11PST |  |  | GUESTROOM201 PTAC DXCOIL | 6.0322 | 3.6412 | 4.5246 | 3.3202 | 3.5639 | 3.8311 | 2.9433 | 3.0186 | 3.1446 | 2.7645 | 2.9988 | 2.8986 | 2.7221 | 2.7017 | 2.3891 | 2.5949
BLD11PST |  |  | GUESTROOM202_205 PTAC DXCOIL | 10.4103 | 10.1164 | 10.9441 | 9.633 | 9.7001 | 10.0381 | 9.7108 | 9.4122 | 9.7866 | 9.5682 | 9.498 | 9.6711 | 9.1002 | 9.3978 | 8.8137 | 9.9084
BLD11PST |  |  | GUESTROOM206_208 PTAC DXCOIL | 8.2615 | 8.0813 | 8.7624 | 7.6967 | 7.9587 | 8.157 | 8.0411 | 7.5423 | 7.929 | 7.9266 | 7.5987 | 7.8329 | 7.3742 | 7.6604 | 7.2563 | 8.3935
BLD11PST |  |  | GUESTROOM209_212 PTAC DXCOIL | 10.2434 | 9.9619 | 10.7631 | 9.4821 | 9.5029 | 9.8275 | 9.5001 | 9.2824 | 9.5754 | 9.3516 | 9.34 | 9.4552 | 8.9416 | 9.1856 | 8.5982 | 9.6289
BLD11PST |  |  | GUESTROOM213 PTAC DXCOIL | 2.9719 | 2.727 | 3.0791 | 2.591 | 2.6119 | 2.7964 | 2.498 | 2.4952 | 2.5443 | 2.4958 | 2.4985 | 2.4703 | 2.3746 | 2.4025 | 2.2428 | 2.4602
BLD11PST |  |  | GUESTROOM214 PTAC DXCOIL | 3.0415 | 2.5764 | 2.8839 | 2.5211 | 2.1157 | 2.6945 | 1.9065 | 2.4424 | 2.4544 | 2.0665 | 2.4361 | 2.3494 | 2.3365 | 2.2541 | 2.0825 | 1.9784
BLD11PST |  |  | GUESTROOM215_218 PTAC DXCOIL | 10.9861 | 9.7362 | 10.1033 | 9.6083 | 8.25 | 9.8442 | 7.8415 | 9.4481 | 9.8984 | 8.2434 | 9.4729 | 9.7139 | 9.1569 | 9.2638 | 8.4894 | 8.1401
BLD11PST |  |  | GUESTROOM219 PTAC DXCOIL | 3.15 | 2.8234 | 3.0657 | 2.8176 | 2.5483 | 2.9982 | 2.4364 | 2.773 | 3.0686 | 2.5564 | 2.7878 | 3.019 | 2.7036 | 2.876 | 2.6372 | 2.5512
BLD11PST |  |  | GUESTROOM220_223 PTAC DXCOIL | 10.5394 | 9.265 | 9.5458 | 9.1126 | 7.6531 | 9.1856 | 7.2199 | 8.9532 | 9.1477 | 7.6176 | 8.9746 | 8.9592 | 8.6605 | 8.5479 | 7.8358 | 7.5029
BLD11PST |  |  | GUESTROOM224 PTAC DXCOIL | 2.9644 | 2.5304 | 2.7616 | 2.3561 | 2.0854 | 2.6077 | 1.915 | 2.4039 | 2.4498 | 2.0531 | 2.4033 | 2.3697 | 2.314 | 2.2673 | 2.0915 | 1.9693
BLD11PST |  |  | GUESTROOM301 PTAC DXCOIL | 6.0056 | 3.6269 | 4.5191 | 3.3093 | 3.5097 | 3.8183 | 2.9099 | 3.0068 | 3.1244 | 2.746 | 2.9714 | 2.8766 | 2.7083 | 2.6828 | 2.3832 | 2.6004
BLD11PST |  |  | GUESTROOM302_305 PTAC DXCOIL | 10.3735 | 10.0229 | 11.0089 | 9.6793 | 9.6546 | 10.1517 | 9.775 | 9.4836 | 9.8769 | 9.6427 | 9.5469 | 9.7646 | 9.1531 | 9.5034 | 8.9204 | 10.0519
BLD11PST |  |  | GUESTROOM306_308 PTAC DXCOIL | 8.2859 | 8.0774 | 8.9094 | 7.8089 | 8.0255 | 8.3541 | 8.2167 | 7.6574 | 8.1001 | 8.1112 | 7.7187 | 8.0092 | 7.5058 | 7.8514 | 7.4555 | 8.6876
BLD11PST |  |  | GUESTROOM309_312 PTAC DXCOIL | 10.3083 | 10.0084 | 10.9891 | 9.667 | 9.639 | 10.1318 | 9.7593 | 9.4712 | 9.8574 | 9.6276 | 9.5345 | 9.744 | 9.142 | 9.4861 | 8.9033 | 10.0272
BLD11PST |  |  | GUESTROOM313 PTAC DXCOIL | 2.9442 | 2.7223 | 3.1244 | 2.6251 | 2.621 | 2.8619 | 2.5485 | 2.5381 | 2.5975 | 2.5531 | 2.5436 | 2.5236 | 2.4228 | 2.4637 | 2.3089 | 2.5533
BLD11PST |  |  | GUESTROOM314 PTAC DXCOIL | 3.0439 | 2.6087 | 2.9468 | 2.4527 | 2.1431 | 2.7674 | 1.9593 | 2.4827 | 2.5098 | 2.123 | 2.4793 | 2.4049 | 2.381 | 2.3145 | 2.1504 | 2.0618
BLD11PST |  |  | GUESTROOM315_318 PTAC DXCOIL | 10.7093 | 9.4766 | 9.8193 | 9.3243 | 7.9045 | 9.5622 | 7.5497 | 9.1945 | 9.511 | 7.948 | 9.2252 | 9.3295 | 8.9143 | 8.9159 | 8.204 | 7.904
BLD11PST |  |  | GUESTROOM319 PTAC DXCOIL | 2.8218 | 2.4775 | 2.6248 | 2.3149 | 2.0912 | 2.5437 | 1.9901 | 2.3929 | 2.5115 | 2.0999 | 2.4059 | 2.4602 | 2.3247 | 2.3512 | 2.165 | 2.075
BLD11PST |  |  | GUESTROOM320_323 PTAC DXCOIL | 10.6067 | 9.3754 | 9.6812 | 9.2204 | 7.7849 | 9.4215 | 7.4299 | 9.0917 | 9.3602 | 7.8241 | 9.1224 | 9.1796 | 8.8123 | 8.7731 | 8.0737 | 7.7753
BLD11PST |  |  | GUESTROOM324 PTAC DXCOIL | 2.9676 | 2.5471 | 2.8115 | 2.3822 | 2.0925 | 2.6614 | 1.9423 | 2.4257 | 2.474 | 2.0844 | 2.4273 | 2.3907 | 2.3386 | 2.294 | 2.1284 | 2.0201
BLD11PST |  |  | GUESTROOM401 PTAC DXCOIL | 6.1014 | 3.7769 | 4.5572 | 3.4683 | 3.6439 | 3.8668 | 2.9847 | 3.0991 | 3.2255 | 2.8096 | 3.0257 | 2.8856 | 2.7006 | 2.6706 | 2.328 | 2.6036
BLD11PST |  |  | GUESTROOM402_405 PTAC DXCOIL | 11.1017 | 10.3587 | 10.5685 | 9.9465 | 9.6519 | 9.9661 | 9.9365 | 9.5188 | 10.0361 | 9.5682 | 9.4974 | 9.5979 | 8.9789 | 9.2945 | 8.5657 | 10.1458
BLD11PST |  |  | GUESTROOM406_408 PTAC DXCOIL | 8.8925 | 8.3751 | 8.572 | 8.0335 | 7.9352 | 8.1712 | 8.3214 | 7.7084 | 8.2116 | 8.0201 | 7.7041 | 7.8638 | 7.3237 | 7.6283 | 7.1383 | 8.8146
BLD11PST |  |  | GUESTROOM409_412 PTAC DXCOIL | 11.0605 | 10.34 | 10.5845 | 9.9507 | 9.6421 | 9.9428 | 9.9339 | 9.5122 | 10.0175 | 9.5683 | 9.4938 | 9.5852 | 9.0058 | 9.2884 | 8.5654 | 10.1412
BLD11PST |  |  | GUESTROOM413 PTAC DXCOIL | 3.1286 | 2.8083 | 3.0077 | 2.6987 | 2.6069 | 2.8272 | 2.5964 | 2.5489 | 2.6504 | 2.5397 | 2.535 | 2.4958 | 2.3839 | 2.4335 | 2.2237 | 2.5753
BLD11PST |  |  | GUESTROOM414 PTAC DXCOIL | 3.1925 | 2.8302 | 3.1035 | 2.78 | 2.4762 | 2.9399 | 2.1812 | 2.51 | 2.7218 | 2.2879 | 2.4899 | 2.5062 | 2.3887 | 2.4005 | 2.2185 | 2.0903
BLD11PST |  |  | GUESTROOM415_418 PTAC DXCOIL | 11.3046 | 10.2362 | 10.3399 | 9.7522 | 9.0701 | 10.1001 | 8.2711 | 9.3433 | 10.1074 | 8.4631 | 9.091 | 9.4989 | 8.5645 | 9.0155 | 8.2832 | 7.9382
BLD11PST |  |  | GUESTROOM419 PTAC DXCOIL | 2.9484 | 2.6402 | 2.7031 | 2.5468 | 2.3607 | 2.621 | 2.1313 | 2.3609 | 2.5989 | 2.1787 | 2.3267 | 2.4253 | 2.195 | 2.304 | 2.1087 | 2.0032
BLD11PST |  |  | GUESTROOM420_423 PTAC DXCOIL | 11.2335 | 10.1672 | 10.2431 | 9.6626 | 8.9887 | 10.0033 | 8.1947 | 9.2774 | 10.0076 | 8.3833 | 9.0254 | 9.402 | 8.4999 | 8.9225 | 8.1977 | 7.8547
BLD11PST |  |  | GUESTROOM424 PTAC DXCOIL | 3.1512 | 2.7556 | 2.9835 | 2.7095 | 2.4264 | 2.834 | 2.1646 | 2.4535 | 2.6731 | 2.2484 | 2.4154 | 2.4682 | 2.3166 | 2.3562 | 2.1694 | 2.0382
BLD11PST |  |  | PSZ-HEATCOOL:1_COOLC DXCOIL | 10.761 | 9.8703 | 9.8775 | 9.6376 | 8.9916 | 9.2464 | 7.2287 | 9.141 | 9.8674 | 8.2458 | 9.1113 | 9.6726 | 9.1069 | 9.2331 | 8.4313 | 7.4184
BLD11PST |  |  | PSZ-HEATCOOL:10_COOLC DXCOIL | 6.9534 | 5.8793 | 6.1717 | 5.5135 | 5.1473 | 5.7811 | 4.6102 | 5.4058 | 5.5777 | 4.8175 | 5.4302 | 5.3829 | 5.201 | 5.136 | 4.8113 | 4.7179
BLD11PST |  |  | PSZ-HEATCOOL:11_COOLC DXCOIL | 6.6215 | 5.5379 | 5.9078 | 5.1907 | 4.7251 | 5.445 | 4.2571 | 5.0958 | 5.1304 | 4.458 | 5.1192 | 4.9336 | 4.8801 | 4.7247 | 4.4585 | 4.4143
BLD11PST |  |  | PSZ-HEATCOOL:12_COOLC DXCOIL | 7.4435 | 6.3593 | 6.3069 | 6.1066 | 5.8966 | 5.891 | 5.0239 | 5.6216 | 5.6874 | 5.0061 | 5.4469 | 5.1043 | 5.0286 | 4.8729 | 4.4422 | 4.2689
BLD11PST |  |  | PSZ-HEATCOOL:2_COOLC DXCOIL | 25.3357 | 21.643 | 24.7762 | 21.5182 | 21.2895 | 22.995 | 16.1854 | 20.2234 | 17.3198 | 17.5137 | 20.3886 | 17.05 | 19.9416 | 15.3935 | 19.6832 | 14.6063
BLD11PST |  |  | PSZ-HEATCOOL:3_COOLC DXCOIL | 1.9651 | 1.6317 | 1.807 | 1.5762 | 1.7032 | 1.6124 | 1.4145 | 1.4895 | 1.5369 | 1.4107 | 1.4712 | 1.4913 | 1.3944 | 1.4271 | 1.2334 | 1.1329
BLD11PST |  |  | PSZ-HEATCOOL:4_COOLC DXCOIL | 13.0615 | 12.1031 | 13.2079 | 12.2463 | 12.94 | 12.8129 | 9.6145 | 11.6111 | 11.8053 | 10.8681 | 11.7341 | 11.7975 | 11.593 | 9.9747 | 11.383 | 7.8951
BLD11PST |  |  | PSZ-HEATCOOL:5_COOLC DXCOIL | 1.7393 | 1.3908 | 1.4338 | 1.2749 | 1.1849 | 1.0866 | 0.88605 | 1.2111 | 0.8905 | 0.86517 | 1.1893 | 0.84473 | 1.0858 | 0.81359 | 0.87837 | 0.92278
BLD11PST |  |  | PSZ-HEATCOOL:6_COOLC DXCOIL | 8.7957 | 8.2162 | 7.5261 | 8.0712 | 6.2894 | 6.5982 | 5.1301 | 8.0466 | 6.3341 | 5.5631 | 8.0418 | 6.278 | 7.7491 | 5.9358 | 6.6748 | 5.0738
BLD11PST |  |  | PSZ-HEATCOOL:7_COOLC DXCOIL | 31.0982 | 30.1595 | 29.1776 | 29.4453 | 25.4153 | 27.2306 | 24.2444 | 28.7911 | 30.1767 | 25.0639 | 28.6803 | 30.057 | 28.554 | 28.4438 | 26.3406 | 24.6508
BLD11PST |  |  | PSZ-HEATCOOL:8_COOLC DXCOIL | 4.2937 | 3.6881 | 3.8689 | 3.7193 | 3.3745 | 3.7306 | 2.181 | 3.4661 | 3.136 | 2.6446 | 3.4718 | 3.1033 | 3.4633 | 2.3749 | 3.2524 | 2.0041
BLD11PST |  |  | PSZ-HEATCOOL:9_COOLC DXCOIL | 13.0856 | 11.086 | 10.3 | 10.5797 | 8.0046 | 8.6063 | 5.7365 | 10.3476 | 7.7275 | 6.5745 | 10.2558 | 7.4588 | 9.7636 | 7.0515 | 7.915 | 5.4022
BLD11PST | HEAT |  | Heating (kW) | 298.184 | 269.9029 | 246.7319 | 288.6891 | 268.3324 | 254.3287 | 269.304 | 299.9559 | 261.4755 | 259.8951 | 350.6096 | 300.508 | 369.7938 | 350.9403 | 372.9051 | 452.5282
BLD11PST |  |  | FRONTSTAIRSFLR1 UNIT HEATER COIL | 0.5352 | 1.1058 | 0.83572 | 1.4786 | 0.40435 | 1.0732 | 0.55618 | 1.6945 | 1.3103 | 1.1138 | 2.5095 | 1.9665 | 2.8776 | 2.7446 | 3.0439 | 4.3695
BLD11PST |  |  | FRONTSTAIRSFLR2 UNIT HEATER COIL | 0.70515 | 1.0713 | 0.81682 | 1.3578 | 0.47591 | 0.98414 | 0.58198 | 1.5135 | 1.1815 | 1.0333 | 2.1842 | 1.7284 | 2.4704 | 2.3627 | 2.5968 | 3.6557
BLD11PST |  |  | FRONTSTAIRSFLR3 UNIT HEATER COIL | 0.74102 | 1.1101 | 0.84191 | 1.3954 | 0.50888 | 1.0109 | 0.62175 | 1.551 | 1.217 | 1.0709 | 2.2167 | 1.7632 | 2.5015 | 2.3957 | 2.6262 | 3.6833
BLD11PST |  |  | FRONTSTAIRSFLR4 UNIT HEATER COIL | 0.79815 | 1.2578 | 0.9178 | 1.5806 | 0.63223 | 1.1162 | 0.76829 | 1.7303 | 1.3914 | 1.2287 | 2.4237 | 1.9588 | 2.7062 | 2.6323 | 2.8232 | 3.8913
BLD11PST |  |  | FRONTSTORAGEFLR1 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10008
BLD11PST |  |  | FRONTSTORAGEFLR2 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0249 | 0.02998 | 0.03208 | 0.11468
BLD11PST |  |  | FRONTSTORAGEFLR3 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03444 | 0 | 0.04695 | 0.05142 | 0.05275 | 0.13169
BLD11PST |  |  | FRONTSTORAGEFLR4 UNIT HEATER COIL | 0 | 0.03004 | 0 | 0.08358 | 0 | 0 | 0 | 0.07224 | 0.04573 | 0 | 0.16022 | 0.11514 | 0.17219 | 0.19347 | 0.17364 | 0.25757
BLD11PST |  |  | GUESTROOM101 PTAC HEAT COIL | 0.73657 | 1.0492 | 0.96079 | 1.2173 | 0.72156 | 1.095 | 0.77901 | 1.3124 | 1.1523 | 1.0578 | 1.6908 | 1.4339 | 1.845 | 1.7752 | 1.9226 | 2.5201
BLD11PST |  |  | GUESTROOM102 PTAC HEAT COIL | 0.75496 | 1.071 | 0.98075 | 1.239 | 0.74053 | 1.1162 | 0.7981 | 1.3338 | 1.1741 | 1.0786 | 1.7138 | 1.4565 | 1.868 | 1.7984 | 1.946 | 2.5448
BLD11PST |  |  | GUESTROOM103 PTAC HEAT COIL | 0.98771 | 1.2953 | 1.214 | 1.4701 | 0.95468 | 1.3457 | 1.0062 | 1.5552 | 1.3979 | 1.2901 | 1.9457 | 1.6865 | 2.0959 | 2.0336 | 2.1717 | 2.7719
BLD11PST |  |  | GUESTROOM104 PTAC HEAT COIL | 0.96682 | 1.2771 | 1.2001 | 1.4564 | 0.94183 | 1.3308 | 0.99846 | 1.547 | 1.3844 | 1.2795 | 1.9351 | 1.6773 | 2.0853 | 2.0227 | 2.1609 | 2.7617
BLD11PST |  |  | GUESTROOM105 PTAC HEAT COIL | 0.74388 | 1.0643 | 0.98018 | 1.239 | 0.73534 | 1.1157 | 0.79698 | 1.3378 | 1.1735 | 1.0777 | 1.719 | 1.4625 | 1.8737 | 1.8042 | 1.9519 | 2.5546
BLD11PST |  |  | GUESTROOM201 PTAC HEAT COIL | 1.7865 | 1.906 | 1.7019 | 2.1398 | 1.3347 | 1.817 | 1.3561 | 2.2212 | 1.9122 | 1.7769 | 2.8524 | 2.3929 | 3.0682 | 2.9633 | 3.1695 | 4.0916
BLD11PST |  |  | GUESTROOM202_205 PTAC HEAT COIL | 3.2294 | 4.0413 | 3.4129 | 4.5315 | 2.7044 | 3.8267 | 2.8686 | 4.8197 | 4.1241 | 3.895 | 6.2049 | 5.1757 | 6.7203 | 6.4074 | 6.9797 | 9.0084
BLD11PST |  |  | GUESTROOM206_208 PTAC HEAT COIL | 2.4246 | 3.1329 | 2.6168 | 3.5116 | 2.0481 | 2.9707 | 2.1755 | 3.7341 | 3.2043 | 3.0115 | 4.8444 | 4.0322 | 5.2488 | 5.0018 | 5.4629 | 7.0718
BLD11PST |  |  | GUESTROOM209_212 PTAC HEAT COIL | 3.1341 | 3.959 | 3.3312 | 4.4471 | 2.6386 | 3.7446 | 2.8127 | 4.7461 | 4.0456 | 3.8295 | 6.1168 | 5.0912 | 6.6355 | 6.3152 | 6.8942 | 8.9134
BLD11PST |  |  | GUESTROOM213 PTAC HEAT COIL | 1.053 | 1.242 | 1.0907 | 1.3688 | 0.89954 | 1.1893 | 0.93433 | 1.433 | 1.2594 | 1.1927 | 1.7861 | 1.5271 | 1.9113 | 1.8385 | 1.9736 | 2.4795
BLD11PST |  |  | GUESTROOM214 PTAC HEAT COIL | 1.0197 | 1.2036 | 1.0588 | 1.3336 | 0.86403 | 1.1562 | 0.90039 | 1.3973 | 1.2219 | 1.1567 | 1.7518 | 1.4938 | 1.8752 | 1.8027 | 1.9377 | 2.4448
BLD11PST |  |  | GUESTROOM215_218 PTAC HEAT COIL | 2.8651 | 3.6827 | 3.0839 | 4.1915 | 2.3589 | 3.5012 | 2.5582 | 4.4913 | 3.7794 | 3.56 | 5.8847 | 4.8544 | 6.407 | 6.0843 | 6.6724 | 8.7278
BLD11PST |  |  | GUESTROOM219 PTAC HEAT COIL | 0.55632 | 0.73442 | 0.61963 | 0.86207 | 0.5786 | 0.68383 | 0.63954 | 0.93685 | 0.74919 | 0.76269 | 1.3007 | 1.0296 | 1.4366 | 1.3542 | 1.5051 | 2.0467
BLD11PST |  |  | GUESTROOM220_223 PTAC HEAT COIL | 2.9872 | 3.8196 | 3.2153 | 4.3251 | 2.503 | 3.6338 | 2.6789 | 4.6281 | 3.9188 | 3.6986 | 6.0137 | 4.9867 | 6.5327 | 6.2105 | 6.796 | 8.8325
BLD11PST |  |  | GUESTROOM224 PTAC HEAT COIL | 0.94965 | 1.1482 | 0.99749 | 1.2856 | 0.79472 | 1.1019 | 0.83301 | 1.3547 | 1.1722 | 1.102 | 1.7233 | 1.4584 | 1.851 | 1.7735 | 1.9156 | 2.4233
BLD11PST |  |  | GUESTROOM301 PTAC HEAT COIL | 1.8516 | 1.9529 | 1.735 | 2.1898 | 1.3799 | 1.847 | 1.3998 | 2.2652 | 1.9513 | 1.8167 | 2.8999 | 2.4349 | 3.111 | 3.0096 | 3.2091 | 4.1236
BLD11PST |  |  | GUESTROOM302_305 PTAC HEAT COIL | 3.3479 | 4.1534 | 3.4509 | 4.6506 | 2.8158 | 3.8684 | 2.9887 | 4.93 | 4.2155 | 4 | 6.319 | 5.2746 | 6.8235 | 6.5161 | 7.0736 | 9.0738
BLD11PST |  |  | GUESTROOM306_308 PTAC HEAT COIL | 2.6338 | 3.3322 | 2.7473 | 3.7126 | 2.241 | 3.1055 | 2.3733 | 3.9237 | 3.3813 | 3.1982 | 5.0416 | 4.2167 | 5.4344 | 5.1926 | 5.6416 | 7.2311
BLD11PST |  |  | GUESTROOM309_312 PTAC HEAT COIL | 3.3084 | 4.131 | 3.424 | 4.6269 | 2.7972 | 3.8453 | 2.9763 | 4.9125 | 4.1966 | 3.9867 | 6.2965 | 5.2536 | 6.8036 | 6.4927 | 7.0547 | 9.0543
BLD11PST |  |  | GUESTROOM313 PTAC HEAT COIL | 1.0919 | 1.2796 | 1.1101 | 1.4078 | 0.93436 | 1.2101 | 0.97064 | 1.4693 | 1.2916 | 1.2272 | 1.8248 | 1.5617 | 1.9472 | 1.8759 | 2.0077 | 2.5078
BLD11PST |  |  | GUESTROOM314 PTAC HEAT COIL | 1.0663 | 1.2492 | 1.0846 | 1.3814 | 0.90598 | 1.1832 | 0.9442 | 1.441 | 1.2618 | 1.1986 | 1.7984 | 1.536 | 1.919 | 1.8482 | 1.9795 | 2.4795
BLD11PST |  |  | GUESTROOM315_318 PTAC HEAT COIL | 3.2656 | 4.0778 | 3.3915 | 4.5881 | 2.7497 | 3.8109 | 2.9307 | 4.8724 | 4.1487 | 3.9401 | 6.2594 | 5.2207 | 6.7641 | 6.4503 | 7.0175 | 9.024
BLD11PST |  |  | GUESTROOM319 PTAC HEAT COIL | 0.83202 | 1.0194 | 0.84526 | 1.1578 | 0.66925 | 0.94981 | 0.70853 | 1.2253 | 1.0355 | 0.9735 | 1.5979 | 1.3217 | 1.7293 | 1.6527 | 1.7948 | 2.3303
BLD11PST |  |  | GUESTROOM320_323 PTAC HEAT COIL | 3.2397 | 4.0576 | 3.3694 | 4.5665 | 2.7332 | 3.7894 | 2.9174 | 4.8537 | 4.1292 | 3.924 | 6.2376 | 5.2006 | 6.7424 | 6.426 | 6.9952 | 8.9943
BLD11PST |  |  | GUESTROOM324 PTAC HEAT COIL | 1.0086 | 1.2053 | 1.0307 | 1.3433 | 0.8481 | 1.1365 | 0.88952 | 1.4092 | 1.222 | 1.1569 | 1.7721 | 1.5091 | 1.897 | 1.8198 | 1.9593 | 2.4586
BLD11PST |  |  | GUESTROOM401 PTAC HEAT COIL | 1.9908 | 2.2261 | 1.8797 | 2.5332 | 1.6401 | 2.0368 | 1.6894 | 2.5906 | 2.2632 | 2.1038 | 3.2738 | 2.7865 | 3.476 | 3.4271 | 3.5589 | 4.4817
BLD11PST |  |  | GUESTROOM402_405 PTAC HEAT COIL | 3.9981 | 5.2436 | 4.0658 | 6.0018 | 3.8771 | 4.6358 | 4.1317 | 6.1965 | 5.4357 | 5.1202 | 7.7664 | 6.6372 | 8.2305 | 8.1354 | 8.4189 | 10.4533
BLD11PST |  |  | GUESTROOM406_408 PTAC HEAT COIL | 3.1753 | 4.229 | 3.2578 | 4.8208 | 3.1146 | 3.7399 | 3.3134 | 4.9633 | 4.3833 | 4.1196 | 6.2284 | 5.3342 | 6.5881 | 6.518 | 6.7454 | 8.3622
BLD11PST |  |  | GUESTROOM409_412 PTAC HEAT COIL | 3.9668 | 5.2285 | 4.0461 | 5.9853 | 3.8649 | 4.6199 | 4.1248 | 6.1855 | 5.4236 | 5.113 | 7.7512 | 6.6232 | 8.2176 | 8.1196 | 8.4071 | 10.4416
BLD11PST |  |  | GUESTROOM413 PTAC HEAT COIL | 1.2512 | 1.551 | 1.2623 | 1.7443 | 1.1979 | 1.4012 | 1.256 | 1.7855 | 1.5961 | 1.5073 | 2.1859 | 1.9017 | 2.2986 | 2.2797 | 2.3439 | 2.8524
BLD11PST |  |  | GUESTROOM414 PTAC HEAT COIL | 1.2343 | 1.5381 | 1.2474 | 1.7391 | 1.1849 | 1.3874 | 1.2466 | 1.7784 | 1.5869 | 1.497 | 2.1825 | 1.8985 | 2.2945 | 2.2772 | 2.3394 | 2.8479
BLD11PST |  |  | GUESTROOM415_418 PTAC HEAT COIL | 3.9564 | 5.2128 | 4.0475 | 5.9857 | 3.8574 | 4.6185 | 4.1226 | 6.1827 | 5.4143 | 5.1072 | 7.7502 | 6.6276 | 8.2155 | 8.1112 | 8.4068 | 10.4391
BLD11PST |  |  | GUESTROOM419 PTAC HEAT COIL | 1.0776 | 1.3986 | 1.0855 | 1.6119 | 1.0384 | 1.2347 | 1.1039 | 1.6562 | 1.4537 | 1.363 | 2.0808 | 1.7817 | 2.2018 | 2.1847 | 2.2499 | 2.7925
BLD11PST |  |  | GUESTROOM420_423 PTAC HEAT COIL | 3.9138 | 5.1717 | 4.0062 | 5.943 | 3.8199 | 4.5773 | 4.0862 | 6.1418 | 5.3732 | 5.0691 | 7.705 | 6.5841 | 8.1706 | 8.0647 | 8.3615 | 10.3901
BLD11PST |  |  | GUESTROOM424 PTAC HEAT COIL | 1.1932 | 1.5125 | 1.2084 | 1.7111 | 1.1509 | 1.3582 | 1.218 | 1.7577 | 1.5642 | 1.4816 | 2.156 | 1.8738 | 2.2713 | 2.2491 | 2.3177 | 2.8256
BLD11PST |  |  | REARSTAIRSFLR1 UNIT HEATER COIL | 0.47638 | 1.0001 | 0.74218 | 1.3577 | 0.32303 | 0.96342 | 0.46482 | 1.5665 | 1.1908 | 1.0033 | 2.3624 | 1.8301 | 2.723 | 2.5937 | 2.8846 | 4.2119
BLD11PST |  |  | REARSTAIRSFLR2 UNIT HEATER COIL | 0.58264 | 0.9408 | 0.68849 | 1.2159 | 0.36334 | 0.85202 | 0.46555 | 1.3716 | 1.0467 | 0.90326 | 2.0249 | 1.577 | 2.3101 | 2.2005 | 2.4361 | 3.496
BLD11PST |  |  | REARSTAIRSFLR3 UNIT HEATER COIL | 0.60584 | 0.9663 | 0.70346 | 1.2417 | 0.38652 | 0.86843 | 0.49202 | 1.3992 | 1.0711 | 0.92899 | 2.0517 | 1.6025 | 2.3373 | 2.2282 | 2.4627 | 3.5202
BLD11PST |  |  | REARSTAIRSFLR4 UNIT HEATER COIL | 0.65517 | 1.0957 | 0.76708 | 1.4135 | 0.49475 | 0.95703 | 0.62553 | 1.5622 | 1.2255 | 1.0708 | 2.2501 | 1.7862 | 2.5317 | 2.4559 | 2.6492 | 3.7164
BLD11PST |  |  | REARSTORAGEFLR1 UNIT HEATER COIL | 0.36573 | 0.56469 | 0.49147 | 0.77614 | 0.18174 | 0.58793 | 0.2171 | 0.83456 | 0.66577 | 0.50688 | 1.2883 | 1.0148 | 1.4491 | 1.4237 | 1.5237 | 2.2063
BLD11PST |  |  | REARSTORAGEFLR2 UNIT HEATER COIL | 0.52861 | 0.61687 | 0.52053 | 0.77602 | 0.27677 | 0.58047 | 0.29817 | 0.80415 | 0.65148 | 0.53034 | 1.1824 | 0.94538 | 1.3031 | 1.2816 | 1.3568 | 1.8919
BLD11PST |  |  | REARSTORAGEFLR3 UNIT HEATER COIL | 0.54783 | 0.63567 | 0.53256 | 0.79408 | 0.29306 | 0.59243 | 0.31538 | 0.82209 | 0.66698 | 0.54713 | 1.1996 | 0.96131 | 1.3198 | 1.2979 | 1.3729 | 1.9055
BLD11PST |  |  | REARSTORAGEFLR4 UNIT HEATER COIL | 0.53559 | 0.64764 | 0.52888 | 0.81269 | 0.30203 | 0.59826 | 0.33135 | 0.8427 | 0.68497 | 0.56592 | 1.222 | 0.98138 | 1.3429 | 1.3218 | 1.3957 | 1.9271
BLD11PST |  |  | PSZ-HEATCOOL:1_HEATC | 30.3554 | 14.3582 | 13.9694 | 14.1367 | 25.8946 | 12.8197 | 20.9804 | 14.0076 | 12.396 | 12.4334 | 14.227 | 12.5104 | 14.35 | 13.027 | 13.288 | 12.9827
BLD11PST |  |  | PSZ-HEATCOOL:10_HEATC | 9.4747 | 8.1231 | 8.8412 | 7.9941 | 7.6669 | 8.2135 | 13.3518 | 8.0178 | 7.3078 | 7.5492 | 8.3378 | 7.3713 | 8.3535 | 7.774 | 8.1501 | 8.8174
BLD11PST |  |  | PSZ-HEATCOOL:11_HEATC | 8.9503 | 7.5981 | 8.4101 | 7.4972 | 7.0828 | 7.7824 | 6.5848 | 7.5159 | 6.797 | 7.0571 | 7.8367 | 6.859 | 7.8574 | 7.2788 | 7.6845 | 8.4026
BLD11PST |  |  | PSZ-HEATCOOL:12_HEATC | 10.322 | 8.9939 | 9.0738 | 9.0681 | 8.7038 | 8.3545 | 7.6493 | 8.4545 | 7.4331 | 7.8075 | 8.4757 | 7.0536 | 8.1535 | 7.4572 | 7.663 | 8.2039
BLD11PST |  |  | PSZ-HEATCOOL:2_HEATC | 30.1153 | 31.9093 | 30.9449 | 33.164 | 29.1327 | 30.6858 | 29.3881 | 34.9326 | 29.6852 | 32.9731 | 39.3046 | 33.2513 | 41.2848 | 38.3846 | 41.654 | 51.9781
BLD11PST |  |  | PSZ-HEATCOOL:3_HEATC | 2.7198 | 2.1779 | 2.4108 | 2.109 | 2.3568 | 2.0691 | 1.9637 | 2.0143 | 1.7558 | 1.9315 | 1.9737 | 1.7007 | 1.8793 | 1.7188 | 1.6276 | 1.5483
BLD11PST |  |  | PSZ-HEATCOOL:4_HEATC | 18.843 | 23.2715 | 20.777 | 25.083 | 19.3885 | 21.8524 | 20.4621 | 27.2226 | 22.8522 | 24.1859 | 31.7509 | 26.7536 | 34.1006 | 31.7488 | 34.6826 | 43.1954
BLD11PST |  |  | PSZ-HEATCOOL:5_HEATC | 2.0934 | 1.6565 | 1.8342 | 1.6301 | 1.7493 | 1.5391 | 1.4056 | 1.5791 | 1.2607 | 1.4325 | 1.6254 | 1.284 | 1.5786 | 1.393 | 1.431 | 1.8774
BLD11PST |  |  | PSZ-HEATCOOL:6_HEATC | 9.7888 | 10.2221 | 9.6393 | 10.4905 | 8.9642 | 9.7269 | 8.8687 | 10.8857 | 9.8634 | 9.8378 | 11.7794 | 10.6206 | 12.2372 | 11.608 | 12.1511 | 13.5863
BLD11PST |  |  | PSZ-HEATCOOL:7_HEATC | 75.8888 | 39.9302 | 38.584 | 40.3828 | 72.7286 | 38.5713 | 70.3009 | 40.9842 | 38.7448 | 38.6649 | 42.3849 | 39.9036 | 43.1381 | 41.5071 | 42.5704 | 44.5041
BLD11PST |  |  | PSZ-HEATCOOL:8_HEATC | 5.7048 | 6.5044 | 5.7549 | 6.9459 | 5.0224 | 5.9823 | 5.0656 | 7.4277 | 6.2197 | 6.2216 | 8.557 | 7.1935 | 9.1808 | 8.4341 | 9.1825 | 11.0541
BLD11PST |  |  | PSZ-HEATCOOL:9_HEATC | 15.2517 | 13.7177 | 13.3457 | 13.5845 | 11.3603 | 12.5631 | 10.0174 | 13.7604 | 11.8135 | 11.6245 | 14.6358 | 12.4392 | 14.973 | 13.5598 | 14.048 | 14.9422
BLD11PST |  |  | HVAC Efficiency
BLD11PST | COP |  | Air Conditioning (COP) | 3.0501 | 3.0635 | 3.0453 | 3.071 | 3.0657 | 3.0504 | 3.0485 | 3.0731 | 3.0614 | 3.0639 | 3.0734 | 3.0669 | 3.0812 | 3.0612 | 3.0786 | 3.0365
BLD11PST |  |  | GUESTROOM101 PTAC DXCOIL | 2.99 | 3.04 | 3.02 | 3.06 | 3.07 | 3.09 | 3.09 | 3.08 | 3.09 | 3.09 | 3.08 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09
BLD11PST |  |  | GUESTROOM102 PTAC DXCOIL | 2.98 | 3.03 | 3.01 | 3.06 | 3.05 | 3.08 | 3.09 | 3.07 | 3.09 | 3.09 | 3.07 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09
BLD11PST |  |  | GUESTROOM103 PTAC DXCOIL | 2.92 | 3 | 2.97 | 3.04 | 3.03 | 3.05 | 3.09 | 3.06 | 3.09 | 3.09 | 3.06 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09
BLD11PST |  |  | GUESTROOM104 PTAC DXCOIL | 2.94 | 3.04 | 3.03 | 3.06 | 3.09 | 3.08 | 3.09 | 3.08 | 3.09 | 3.09 | 3.08 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09
BLD11PST |  |  | GUESTROOM105 PTAC DXCOIL | 2.97 | 3.05 | 3.06 | 3.06 | 3.09 | 3.09 | 3.09 | 3.07 | 3.09 | 3.09 | 3.07 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09
BLD11PST |  |  | GUESTROOM201 PTAC DXCOIL | 2.67 | 2.8 | 2.67 | 2.86 | 2.82 | 2.77 | 2.93 | 2.92 | 2.9 | 2.96 | 2.92 | 2.94 | 2.97 | 2.98 | 3.03 | 3
BLD11PST |  |  | GUESTROOM202_205 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM206_208 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM209_212 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM213 PTAC DXCOIL | 2.93 | 2.97 | 2.91 | 3 | 2.99 | 2.96 | 3.01 | 3.01 | 3 | 3.01 | 3.01 | 3.02 | 3.04 | 3.03 | 3.06 | 3.02
BLD11PST |  |  | GUESTROOM214 PTAC DXCOIL | 2.91 | 3 | 2.94 | 3.01 | 3.08 | 2.98 | 3.09 | 3.02 | 3.02 | 3.09 | 3.02 | 3.04 | 3.04 | 3.06 | 3.09 | 3.09
BLD11PST |  |  | GUESTROOM215_218 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM219 PTAC DXCOIL | 2.89 | 2.95 | 2.91 | 2.95 | 3 | 2.92 | 3.02 | 2.96 | 2.91 | 3 | 2.96 | 2.92 | 2.98 | 2.94 | 2.99 | 3
BLD11PST |  |  | GUESTROOM220_223 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM224 PTAC DXCOIL | 2.93 | 3.01 | 2.96 | 3.04 | 3.09 | 2.99 | 3.09 | 3.03 | 3.02 | 3.09 | 3.03 | 3.04 | 3.05 | 3.05 | 3.09 | 3.09
BLD11PST |  |  | GUESTROOM301 PTAC DXCOIL | 2.67 | 2.81 | 2.67 | 2.87 | 2.83 | 2.77 | 2.94 | 2.92 | 2.9 | 2.97 | 2.93 | 2.94 | 2.97 | 2.98 | 3.03 | 2.99
BLD11PST |  |  | GUESTROOM302_305 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM306_308 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM309_312 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM313 PTAC DXCOIL | 2.93 | 2.97 | 2.9 | 2.99 | 2.99 | 2.95 | 3 | 3.01 | 2.99 | 3 | 3 | 3.01 | 3.03 | 3.02 | 3.05 | 3
BLD11PST |  |  | GUESTROOM314 PTAC DXCOIL | 2.91 | 2.99 | 2.93 | 3.02 | 3.08 | 2.96 | 3.09 | 3.02 | 3.01 | 3.08 | 3.02 | 3.03 | 3.03 | 3.05 | 3.08 | 3.09
BLD11PST |  |  | GUESTROOM315_318 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM319 PTAC DXCOIL | 2.95 | 3.02 | 2.99 | 3.05 | 3.09 | 3 | 3.09 | 3.03 | 3.01 | 3.09 | 3.03 | 3.02 | 3.04 | 3.04 | 3.07 | 3.09
BLD11PST |  |  | GUESTROOM320_323 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM324 PTAC DXCOIL | 2.93 | 3 | 2.96 | 3.03 | 3.09 | 2.98 | 3.09 | 3.03 | 3.02 | 3.09 | 3.03 | 3.03 | 3.04 | 3.05 | 3.08 | 3.09
BLD11PST |  |  | GUESTROOM401 PTAC DXCOIL | 2.67 | 2.78 | 2.67 | 2.84 | 2.8 | 2.76 | 2.92 | 2.9 | 2.88 | 2.96 | 2.92 | 2.94 | 2.98 | 2.98 | 3.04 | 2.99
BLD11PST |  |  | GUESTROOM402_405 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM406_408 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM409_412 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM413 PTAC DXCOIL | 2.9 | 2.96 | 2.92 | 2.98 | 2.99 | 2.95 | 2.99 | 3 | 2.98 | 3.01 | 3.01 | 3.01 | 3.03 | 3.02 | 3.06 | 3
BLD11PST |  |  | GUESTROOM414 PTAC DXCOIL | 2.89 | 2.95 | 2.9 | 2.96 | 3.02 | 2.93 | 3.07 | 3.01 | 2.97 | 3.05 | 3.01 | 3.01 | 3.03 | 3.03 | 3.06 | 3.09
BLD11PST |  |  | GUESTROOM415_418 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM419 PTAC DXCOIL | 2.93 | 2.99 | 2.98 | 3 | 3.04 | 2.99 | 3.08 | 3.04 | 2.99 | 3.07 | 3.04 | 3.03 | 3.07 | 3.05 | 3.08 | 3.09
BLD11PST |  |  | GUESTROOM420_423 PTAC DXCOIL | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67 | 2.67
BLD11PST |  |  | GUESTROOM424 PTAC DXCOIL | 2.89 | 2.97 | 2.92 | 2.97 | 3.03 | 2.95 | 3.07 | 3.02 | 2.98 | 3.06 | 3.03 | 3.02 | 3.05 | 3.04 | 3.07 | 3.09
BLD11PST |  |  | PSZ-HEATCOOL:1_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11PST |  |  | PSZ-HEATCOOL:10_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11PST |  |  | PSZ-HEATCOOL:11_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11PST |  |  | PSZ-HEATCOOL:12_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11PST |  |  | PSZ-HEATCOOL:2_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.67 | 3.5 | 3.67
BLD11PST |  |  | PSZ-HEATCOOL:3_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11PST |  |  | PSZ-HEATCOOL:4_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11PST |  |  | PSZ-HEATCOOL:5_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11PST |  |  | PSZ-HEATCOOL:6_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11PST |  |  | PSZ-HEATCOOL:7_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
BLD11PST |  |  | PSZ-HEATCOOL:8_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11PST |  |  | PSZ-HEATCOOL:9_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11PST | EffHeat |  | Heating Efficiency (%) | 0.84768 | 0.87517 | 0.8674 | 0.88078 | 0.84547 | 0.87405 | 0.84919 | 0.88211 | 0.88058 | 0.87555 | 0.89111 | 0.88889 | 0.89341 | 0.8952 | 0.89588 | 0.90229
BLD11PST |  |  | FRONTSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | FRONTSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | FRONTSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | FRONTSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | FRONTSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | FRONTSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | FRONTSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | FRONTSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM101 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM102 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM103 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM104 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM105 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM201 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM202_205 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM206_208 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM209_212 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM213 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM214 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM215_218 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM219 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM220_223 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM224 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM301 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM302_305 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM306_308 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM309_312 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM313 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM314 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM315_318 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM319 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM320_323 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM324 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM401 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM402_405 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM406_408 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM409_412 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM413 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM414 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM415_418 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM419 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM420_423 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | GUESTROOM424 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | REARSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | REARSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | REARSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | REARSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | REARSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | REARSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | REARSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | REARSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11PST |  |  | PSZ-HEATCOOL:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:10_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:11_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:12_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:7_HEATC | 0.78 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | PSZ-HEATCOOL:9_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11PST |  |  | HVAC Control - Economizer
BLD11PST |  |  | All GuestRoom & UnitHeater systems | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:1 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:10 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:11 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:12 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:6 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:7 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:8 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST |  |  | PSZ-HEATCOOL:9 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11PST | Fan |  | Fan Max Flow Rate (m3/s ) | 19.15 | 16.84 | 18.84 | 17.09 | 16.63 | 18.13 | 15.74 | 16.15 | 18.11 | 16.12 | 16.48 | 17.8 | 16.27 | 17.33 | 16.06 | 16.88
BLD11PST |  |  | FRONTSTAIRSFLR1 UNIT HEATERFAN | 0.02 | 0.04 | 0.03 | 0.05 | 0.01 | 0.04 | 0.02 | 0.06 | 0.05 | 0.04 | 0.09 | 0.08 | 0.1 | 0.11 | 0.11 | 0.15
BLD11PST |  |  | FRONTSTAIRSFLR2 UNIT HEATERFAN | 0.02 | 0.04 | 0.03 | 0.05 | 0.02 | 0.04 | 0.02 | 0.05 | 0.05 | 0.03 | 0.07 | 0.07 | 0.08 | 0.09 | 0.09 | 0.12
BLD11PST |  |  | FRONTSTAIRSFLR3 UNIT HEATERFAN | 0.02 | 0.04 | 0.03 | 0.05 | 0.02 | 0.04 | 0.02 | 0.05 | 0.05 | 0.04 | 0.08 | 0.07 | 0.09 | 0.09 | 0.09 | 0.12
BLD11PST |  |  | FRONTSTAIRSFLR4 UNIT HEATERFAN | 0.03 | 0.04 | 0.03 | 0.05 | 0.02 | 0.04 | 0.03 | 0.06 | 0.06 | 0.04 | 0.08 | 0.08 | 0.09 | 0.1 | 0.1 | 0.13
BLD11PST |  |  | FRONTSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | FRONTSTORAGEFLR2 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | FRONTSTORAGEFLR3 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | FRONTSTORAGEFLR4 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.01
BLD11PST |  |  | GUESTROOM101 PTACFAN | 0.14 | 0.12 | 0.13 | 0.12 | 0.13 | 0.12 | 0.12 | 0.11 | 0.12 | 0.12 | 0.11 | 0.12 | 0.11 | 0.11 | 0.1 | 0.11
BLD11PST |  |  | GUESTROOM102 PTACFAN | 0.14 | 0.12 | 0.14 | 0.12 | 0.14 | 0.13 | 0.12 | 0.11 | 0.12 | 0.12 | 0.11 | 0.12 | 0.11 | 0.12 | 0.11 | 0.11
BLD11PST |  |  | GUESTROOM103 PTACFAN | 0.17 | 0.13 | 0.16 | 0.13 | 0.14 | 0.14 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.1 | 0.1
BLD11PST |  |  | GUESTROOM104 PTACFAN | 0.17 | 0.13 | 0.14 | 0.12 | 0.11 | 0.13 | 0.08 | 0.11 | 0.11 | 0.09 | 0.11 | 0.11 | 0.11 | 0.1 | 0.09 | 0.08
BLD11PST |  |  | GUESTROOM105 PTACFAN | 0.15 | 0.12 | 0.13 | 0.12 | 0.11 | 0.12 | 0.09 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.11 | 0.1 | 0.09
BLD11PST |  |  | GUESTROOM201 PTACFAN | 0.36 | 0.2 | 0.27 | 0.19 | 0.22 | 0.23 | 0.18 | 0.17 | 0.19 | 0.17 | 0.17 | 0.18 | 0.15 | 0.16 | 0.14 | 0.16
BLD11PST |  |  | GUESTROOM202_205 PTACFAN | 0.56 | 0.53 | 0.63 | 0.54 | 0.59 | 0.61 | 0.59 | 0.52 | 0.59 | 0.58 | 0.53 | 0.58 | 0.52 | 0.57 | 0.53 | 0.6
BLD11PST |  |  | GUESTROOM206_208 PTACFAN | 0.45 | 0.43 | 0.51 | 0.44 | 0.48 | 0.49 | 0.49 | 0.42 | 0.48 | 0.48 | 0.43 | 0.47 | 0.42 | 0.46 | 0.44 | 0.51
BLD11PST |  |  | GUESTROOM209_212 PTACFAN | 0.55 | 0.52 | 0.61 | 0.53 | 0.57 | 0.59 | 0.57 | 0.51 | 0.58 | 0.56 | 0.51 | 0.57 | 0.51 | 0.55 | 0.52 | 0.58
BLD11PST |  |  | GUESTROOM213 PTACFAN | 0.17 | 0.15 | 0.18 | 0.15 | 0.16 | 0.17 | 0.15 | 0.14 | 0.15 | 0.15 | 0.14 | 0.15 | 0.14 | 0.15 | 0.14 | 0.15
BLD11PST |  |  | GUESTROOM214 PTACFAN | 0.18 | 0.15 | 0.17 | 0.15 | 0.13 | 0.16 | 0.12 | 0.14 | 0.15 | 0.12 | 0.14 | 0.14 | 0.13 | 0.14 | 0.13 | 0.12
BLD11PST |  |  | GUESTROOM215_218 PTACFAN | 0.63 | 0.54 | 0.61 | 0.54 | 0.5 | 0.59 | 0.47 | 0.52 | 0.6 | 0.5 | 0.52 | 0.59 | 0.52 | 0.56 | 0.51 | 0.49
BLD11PST |  |  | GUESTROOM219 PTACFAN | 0.19 | 0.17 | 0.19 | 0.17 | 0.15 | 0.18 | 0.15 | 0.16 | 0.19 | 0.15 | 0.16 | 0.18 | 0.16 | 0.17 | 0.16 | 0.15
BLD11PST |  |  | GUESTROOM220_223 PTACFAN | 0.59 | 0.51 | 0.57 | 0.5 | 0.46 | 0.55 | 0.44 | 0.48 | 0.55 | 0.46 | 0.49 | 0.54 | 0.48 | 0.52 | 0.47 | 0.45
BLD11PST |  |  | GUESTROOM224 PTACFAN | 0.17 | 0.14 | 0.17 | 0.14 | 0.13 | 0.16 | 0.12 | 0.13 | 0.15 | 0.12 | 0.13 | 0.14 | 0.13 | 0.14 | 0.13 | 0.12
BLD11PST |  |  | GUESTROOM301 PTACFAN | 0.36 | 0.2 | 0.27 | 0.19 | 0.21 | 0.23 | 0.18 | 0.17 | 0.19 | 0.17 | 0.17 | 0.17 | 0.15 | 0.16 | 0.14 | 0.16
BLD11PST |  |  | GUESTROOM302_305 PTACFAN | 0.56 | 0.53 | 0.63 | 0.54 | 0.58 | 0.61 | 0.59 | 0.52 | 0.6 | 0.58 | 0.53 | 0.59 | 0.52 | 0.57 | 0.54 | 0.61
BLD11PST |  |  | GUESTROOM306_308 PTACFAN | 0.45 | 0.43 | 0.52 | 0.45 | 0.48 | 0.5 | 0.5 | 0.43 | 0.49 | 0.49 | 0.44 | 0.48 | 0.43 | 0.47 | 0.45 | 0.52
BLD11PST |  |  | GUESTROOM309_312 PTACFAN | 0.56 | 0.52 | 0.63 | 0.54 | 0.58 | 0.61 | 0.59 | 0.52 | 0.6 | 0.58 | 0.53 | 0.59 | 0.52 | 0.57 | 0.54 | 0.61
BLD11PST |  |  | GUESTROOM313 PTACFAN | 0.17 | 0.15 | 0.19 | 0.15 | 0.16 | 0.17 | 0.15 | 0.14 | 0.16 | 0.15 | 0.14 | 0.15 | 0.14 | 0.15 | 0.14 | 0.15
BLD11PST |  |  | GUESTROOM314 PTACFAN | 0.18 | 0.15 | 0.18 | 0.15 | 0.13 | 0.17 | 0.12 | 0.14 | 0.15 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
BLD11PST |  |  | GUESTROOM315_318 PTACFAN | 0.61 | 0.52 | 0.59 | 0.52 | 0.48 | 0.58 | 0.46 | 0.5 | 0.57 | 0.48 | 0.51 | 0.56 | 0.5 | 0.54 | 0.5 | 0.48
BLD11PST |  |  | GUESTROOM319 PTACFAN | 0.16 | 0.14 | 0.16 | 0.14 | 0.13 | 0.15 | 0.12 | 0.13 | 0.15 | 0.13 | 0.13 | 0.15 | 0.13 | 0.14 | 0.13 | 0.13
BLD11PST |  |  | GUESTROOM320_323 PTACFAN | 0.6 | 0.51 | 0.58 | 0.51 | 0.47 | 0.57 | 0.45 | 0.49 | 0.57 | 0.47 | 0.5 | 0.55 | 0.49 | 0.53 | 0.49 | 0.47
BLD11PST |  |  | GUESTROOM324 PTACFAN | 0.17 | 0.14 | 0.17 | 0.14 | 0.13 | 0.16 | 0.12 | 0.13 | 0.15 | 0.13 | 0.14 | 0.14 | 0.13 | 0.14 | 0.13 | 0.12
BLD11PST |  |  | GUESTROOM401 PTACFAN | 0.37 | 0.21 | 0.28 | 0.21 | 0.22 | 0.23 | 0.18 | 0.18 | 0.19 | 0.17 | 0.17 | 0.17 | 0.16 | 0.16 | 0.14 | 0.16
BLD11PST |  |  | GUESTROOM402_405 PTACFAN | 0.62 | 0.57 | 0.62 | 0.59 | 0.58 | 0.6 | 0.6 | 0.54 | 0.61 | 0.58 | 0.54 | 0.58 | 0.53 | 0.56 | 0.52 | 0.61
BLD11PST |  |  | GUESTROOM406_408 PTACFAN | 0.5 | 0.47 | 0.5 | 0.48 | 0.48 | 0.49 | 0.5 | 0.44 | 0.5 | 0.48 | 0.44 | 0.48 | 0.43 | 0.46 | 0.43 | 0.53
BLD11PST |  |  | GUESTROOM409_412 PTACFAN | 0.62 | 0.57 | 0.61 | 0.59 | 0.58 | 0.6 | 0.6 | 0.54 | 0.61 | 0.58 | 0.54 | 0.58 | 0.53 | 0.56 | 0.52 | 0.61
BLD11PST |  |  | GUESTROOM413 PTACFAN | 0.18 | 0.16 | 0.18 | 0.16 | 0.16 | 0.17 | 0.16 | 0.15 | 0.16 | 0.15 | 0.15 | 0.15 | 0.14 | 0.15 | 0.13 | 0.16
BLD11PST |  |  | GUESTROOM414 PTACFAN | 0.19 | 0.17 | 0.19 | 0.17 | 0.15 | 0.18 | 0.13 | 0.15 | 0.16 | 0.14 | 0.15 | 0.15 | 0.14 | 0.15 | 0.13 | 0.13
BLD11PST |  |  | GUESTROOM415_418 PTACFAN | 0.66 | 0.58 | 0.62 | 0.59 | 0.55 | 0.61 | 0.5 | 0.54 | 0.61 | 0.51 | 0.53 | 0.57 | 0.52 | 0.54 | 0.5 | 0.48
BLD11PST |  |  | GUESTROOM419 PTACFAN | 0.17 | 0.15 | 0.16 | 0.15 | 0.14 | 0.16 | 0.13 | 0.14 | 0.16 | 0.13 | 0.14 | 0.15 | 0.13 | 0.14 | 0.13 | 0.12
BLD11PST |  |  | GUESTROOM420_423 PTACFAN | 0.65 | 0.58 | 0.62 | 0.58 | 0.54 | 0.6 | 0.5 | 0.53 | 0.6 | 0.51 | 0.53 | 0.57 | 0.51 | 0.54 | 0.5 | 0.47
BLD11PST |  |  | GUESTROOM424 PTACFAN | 0.19 | 0.16 | 0.18 | 0.16 | 0.15 | 0.17 | 0.13 | 0.15 | 0.16 | 0.14 | 0.15 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
BLD11PST |  |  | REARSTAIRSFLR1 UNIT HEATERFAN | 0.02 | 0.03 | 0.03 | 0.05 | 0.01 | 0.03 | 0.02 | 0.05 | 0.05 | 0.03 | 0.08 | 0.07 | 0.09 | 0.1 | 0.1 | 0.14
BLD11PST |  |  | REARSTAIRSFLR2 UNIT HEATERFAN | 0.02 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.05 | 0.04 | 0.03 | 0.07 | 0.06 | 0.08 | 0.08 | 0.09 | 0.12
BLD11PST |  |  | REARSTAIRSFLR3 UNIT HEATERFAN | 0.02 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.05 | 0.04 | 0.03 | 0.07 | 0.07 | 0.08 | 0.09 | 0.09 | 0.12
BLD11PST |  |  | REARSTAIRSFLR4 UNIT HEATERFAN | 0.02 | 0.04 | 0.03 | 0.05 | 0.02 | 0.03 | 0.02 | 0.05 | 0.05 | 0.04 | 0.08 | 0.07 | 0.09 | 0.09 | 0.09 | 0.13
BLD11PST |  |  | REARSTORAGEFLR1 UNIT HEATERFAN | 0.01 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.07
BLD11PST |  |  | REARSTORAGEFLR2 UNIT HEATERFAN | 0.02 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.06
BLD11PST |  |  | REARSTORAGEFLR3 UNIT HEATERFAN | 0.02 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.06
BLD11PST |  |  | REARSTORAGEFLR4 UNIT HEATERFAN | 0.02 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.07
BLD11PST |  |  | PSZ-HEATCOOL:1_FAN | 0.63 | 0.58 | 0.6 | 0.58 | 0.54 | 0.56 | 0.44 | 0.55 | 0.6 | 0.5 | 0.55 | 0.58 | 0.55 | 0.56 | 0.51 | 0.45
BLD11PST |  |  | PSZ-HEATCOOL:10_FAN | 0.39 | 0.32 | 0.37 | 0.31 | 0.31 | 0.35 | 0.28 | 0.3 | 0.34 | 0.29 | 0.3 | 0.33 | 0.3 | 0.31 | 0.29 | 0.29
BLD11PST |  |  | PSZ-HEATCOOL:11_FAN | 0.37 | 0.29 | 0.35 | 0.29 | 0.29 | 0.33 | 0.26 | 0.28 | 0.31 | 0.27 | 0.28 | 0.3 | 0.27 | 0.29 | 0.27 | 0.27
BLD11PST |  |  | PSZ-HEATCOOL:12_FAN | 0.43 | 0.35 | 0.38 | 0.36 | 0.36 | 0.36 | 0.3 | 0.32 | 0.34 | 0.3 | 0.31 | 0.31 | 0.29 | 0.29 | 0.27 | 0.26
BLD11PST |  |  | PSZ-HEATCOOL:2_FAN | 1.02 | 0.87 | 1 | 0.87 | 0.95 | 0.94 | 0.88 | 0.81 | 0.9 | 0.89 | 0.82 | 0.88 | 0.8 | 0.85 | 0.79 | 0.88
BLD11PST |  |  | PSZ-HEATCOOL:3_FAN | 0.12 | 0.1 | 0.11 | 0.1 | 0.1 | 0.1 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.08 | 0.09 | 0.07 | 0.07
BLD11PST |  |  | PSZ-HEATCOOL:4_FAN | 0.53 | 0.49 | 0.53 | 0.49 | 0.52 | 0.52 | 0.49 | 0.47 | 0.53 | 0.49 | 0.47 | 0.52 | 0.47 | 0.5 | 0.46 | 0.47
BLD11PST |  |  | PSZ-HEATCOOL:5_FAN | 0.09 | 0.06 | 0.08 | 0.06 | 0.07 | 0.06 | 0.05 | 0.06 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.06
BLD11PST |  |  | PSZ-HEATCOOL:6_FAN | 0.37 | 0.34 | 0.35 | 0.34 | 0.32 | 0.35 | 0.3 | 0.33 | 0.38 | 0.32 | 0.33 | 0.38 | 0.33 | 0.36 | 0.32 | 0.31
BLD11PST |  |  | PSZ-HEATCOOL:7_FAN | 1.6 | 1.57 | 1.61 | 1.61 | 1.53 | 1.65 | 1.46 | 1.55 | 1.82 | 1.51 | 1.57 | 1.82 | 1.58 | 1.72 | 1.57 | 1.49
BLD11PST |  |  | PSZ-HEATCOOL:8_FAN | 0.17 | 0.15 | 0.16 | 0.15 | 0.14 | 0.15 | 0.12 | 0.14 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
BLD11PST |  |  | PSZ-HEATCOOL:9_FAN | 0.6 | 0.48 | 0.51 | 0.46 | 0.42 | 0.47 | 0.34 | 0.43 | 0.47 | 0.38 | 0.43 | 0.45 | 0.42 | 0.43 | 0.38 | 0.33
BLD11PST |  | Utility Costs
BLD11PST |  |  | Electric Utility Rates
BLD11PST |  |  | Average Annual Rate ($/kWh) | 0.078714 | 0.10821 | 0.085704 | 0.10024 | 0.12301 | 0.094839 | 0.14498 | 0.069179 | 0.037181 | 0.071827 | 0.097435 | 0.037188 | 0.054981 | 0.071182 | 0.05486 | 0.090867
BLD11PST |  |  | Total Cost ($/m2) | 19.26 | 23.46 | 18.95 | 20.01 | 23.22 | 19.34 | 25.37 | 13.3 | 7.04 | 12.48 | 18.53 | 6.86 | 10.66 | 13 | 10.32 | 18.89
BLD11PST |  |  | Gas Utility Rates
BLD11PST |  |  | Average Annual Rate ($/MJ) | 0.011458 | 0.008172 | 0.0085268 | 0.010523 | 0.008422 | 0.0080497 | 0.008427 | 0.0099666 | 0.0071319 | 0.0083147 | 0.0087267 | 0.0071279 | 0.0079418 | 0.008566 | 0.0079391 | 0.0041654
BLD11PST |  |  | Total Cost ($/m2) | 1.29 | 1.24 | 1.17 | 1.98 | 1.28 | 1.3 | 1.62 | 2.35 | 1.45 | 1.92 | 2.43 | 1.73 | 2.56 | 2.51 | 2.97 | 2.16
BLD11PST |  |  | Total Utility Costs
BLD11PST |  |  | Cost Intensity ($/m2) | 20.55 | 24.69 | 20.13 | 21.98 | 24.5 | 20.64 | 26.99 | 15.65 | 8.49 | 14.41 | 20.96 | 8.58 | 13.21 | 15.51 | 13.29 | 21.05
BLD11PST |  | Energy - End Uses
BLD11PST |  |  | Electricity (kWh)
BLD11PST |  |  | Heating | 166.6667 | 3888.8889 | 1438.8889 | 9580.5556 | 136.1111 | 2430.5556 | 800 | 16163.8889 | 6875 | 6383.3333 | 31119.4444 | 15913.8889 | 51611.1111 | 34016.6667 | 63533.3333 | 156894.4444
BLD11PST |  |  | Cooling | 325050 | 223766.6667 | 236666.6667 | 152050 | 119663.8889 | 172019.4444 | 72813.8889 | 121883.3333 | 111500 | 61677.7778 | 99383.3333 | 85777.7778 | 93611.1111 | 64638.8889 | 62408.3333 | 48891.6667
BLD11PST |  |  | Interior Lighting | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667
BLD11PST |  |  | Exterior Lighting | 73086.1111 | 72955.5556 | 72936.1111 | 73058.3333 | 73044.4444 | 72972.2222 | 72894.4444 | 72969.4444 | 72955.5556 | 72847.2222 | 72869.4444 | 72880.5556 | 72927.7778 | 72838.8889 | 72819.4444 | 72383.3333
BLD11PST |  |  | Interior Equipment | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667
BLD11PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Fans | 85413.8889 | 70988.8889 | 78191.6667 | 67872.2222 | 66447.2222 | 72516.6667 | 57347.2222 | 62311.1111 | 70236.1111 | 58297.2222 | 61588.8889 | 67033.3333 | 61336.1111 | 63027.7778 | 57927.7778 | 57922.2222
BLD11PST |  |  | Pumps | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475
BLD11PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Total End Uses | 982125 | 870008.3333 | 887641.6667 | 800969.4444 | 757697.2222 | 818347.2222 | 702266.6667 | 771736.1111 | 759977.7778 | 697611.1111 | 763366.6667 | 740013.8889 | 777891.6667 | 732930.5556 | 755097.2222 | 834500
BLD11PST |  |  | Gas (MJ)
BLD11PST |  |  | Heating | 9400 | 113800 | 87780 | 211400 | 75460 | 147830 | 197900 | 362600 | 242910 | 325610 | 501840 | 359110 | 647720 | 524300 | 809640 | 1329150
BLD11PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Equipment | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480
BLD11PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Water Systems | 253600 | 304660 | 275330 | 353800 | 344260 | 310670 | 386330 | 392430 | 385130 | 412550 | 426360 | 424590 | 455670 | 460990 | 504000 | 562480
BLD11PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Total End Uses | 452480 | 607940 | 552590 | 754680 | 609190 | 647980 | 773710 | 944500 | 817520 | 927640 | 1117680 | 973180 | 1292860 | 1174770 | 1503110 | 2081110
BLD11PST |  |  | Purchased Cooling (MJ)
BLD11PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Purchased Heating (MJ)
BLD11PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Total Building (MJ) | 3988130 | 3739970 | 3748090 | 3638170 | 3336900 | 3594030 | 3301870 | 3722760 | 3553440 | 3439040 | 3865800 | 3637230 | 4093280 | 3813330 | 4221460 | 5085310
BLD11PST |  | Energy - End Use Intensities
BLD11PST |  |  | Electricity (MJ/m2)
BLD11PST |  |  | Heating (elec) | 0.14949 | 3.4881 | 1.2906 | 8.5933 | 0.12209 | 2.1801 | 0.71756 | 14.4982 | 6.1665 | 5.7255 | 27.9127 | 14.274 | 46.2927 | 30.5113 | 56.9864 | 140.7269
BLD11PST |  |  | Cooling (elec) | 291.5544 | 200.7081 | 212.2788 | 136.3816 | 107.3328 | 154.2933 | 65.3106 | 109.3236 | 100.0102 | 55.322 | 89.1421 | 76.9386 | 83.9647 | 57.978 | 55.9773 | 43.8535
BLD11PST |  |  | Interior Lighting (elec) | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551 | 244.2551
BLD11PST |  |  | Exterior Lighting (elec) | 65.5548 | 65.4377 | 65.4202 | 65.5299 | 65.5174 | 65.4526 | 65.3829 | 65.4501 | 65.4377 | 65.3405 | 65.3604 | 65.3704 | 65.4128 | 65.333 | 65.3156 | 64.9244
BLD11PST |  |  | Interior Equipment (elec) | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675
BLD11PST |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Fans (elec) | 76.6122 | 63.6737 | 70.1342 | 60.8782 | 59.6 | 65.044 | 51.4377 | 55.8901 | 62.9985 | 52.2898 | 55.2423 | 60.1257 | 55.0156 | 56.5329 | 51.9585 | 51.9535
BLD11PST |  |  | Pumps (elec) | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605
BLD11PST |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Total End Uses | 880.9196 | 780.3562 | 796.1725 | 718.4316 | 679.6185 | 734.0187 | 629.8999 | 692.2107 | 681.664 | 625.7241 | 684.7037 | 663.7574 | 697.732 | 657.404 | 677.2864 | 748.5069
BLD11PST |  |  | Gas (MJ/m2)
BLD11PST |  |  | Heating (gas) | 2.342 | 28.3537 | 21.8707 | 52.6711 | 18.8011 | 36.8324 | 49.3075 | 90.3431 | 60.5219 | 81.1269 | 125.0352 | 89.4735 | 161.3817 | 130.6312 | 201.7246 | 331.1624
BLD11PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Equipment (gas) | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096
BLD11PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Water Systems (gas) | 63.1853 | 75.9071 | 68.5994 | 88.1505 | 85.7736 | 77.4045 | 96.2555 | 97.7753 | 95.9565 | 102.7883 | 106.2291 | 105.7881 | 113.5318 | 114.8573 | 125.5734 | 140.1439
BLD11PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Total End Uses | 112.737 | 151.4704 | 137.6797 | 188.0312 | 151.7818 | 161.4465 | 192.7726 | 235.3255 | 203.688 | 231.1248 | 278.4739 | 242.4712 | 322.1206 | 292.6981 | 374.5051 | 518.5158
BLD11PST |  |  | Purchased Cooling (MJ/m2)
BLD11PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Purchased Heating (MJ/m2)
BLD11PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Total Building (MJ/m2) | 993.6566 | 931.8266 | 933.8497 | 906.4628 | 831.4003 | 895.4652 | 822.6725 | 927.5387 | 885.352 | 856.8489 | 963.1776 | 906.2286 | 1019.855 | 950.1045 | 1051.7915 | 1267.0228
BLD11PST |  | Peak Energy Demand
BLD11PST |  |  | Electricity Peak Demand (kW)
BLD11PST |  |  | Jan | 163.8692 | 155.7972 | 141.8598 | 139.3516 | 139.3035 | 130.3249 | 132.2019 | 142.3616 | 131.0793 | 126.2136 | 160.1061 | 146.4307 | 173.5209 | 174.6276 | 174.0099 | 230.8436
BLD11PST |  |  | Feb | 166.4623 | 149.806 | 141.883 | 140.839 | 140.2827 | 135.3519 | 137.8021 | 130.5267 | 134.2458 | 131.8798 | 133.403 | 135.3826 | 157.1136 | 151.0714 | 175.6861 | 230.5803
BLD11PST |  |  | Mar | 171.1002 | 161.9719 | 162.4814 | 147.9653 | 138.7387 | 139.7759 | 134.358 | 144.7123 | 137.1626 | 138.7486 | 138.1487 | 139.1056 | 137.33 | 136.3255 | 143.9479 | 179.9276
BLD11PST |  |  | Apr | 177.4465 | 172.5699 | 163.2725 | 158.8234 | 147.4546 | 159.4369 | 139.8972 | 145.3023 | 148.8211 | 139.7202 | 137.4179 | 144.6272 | 147.0344 | 136.5942 | 133.2728 | 131.6024
BLD11PST |  |  | May | 182.0496 | 183.9901 | 188.6666 | 172.8288 | 149.5226 | 168.6513 | 141.1603 | 158.5432 | 155.982 | 144.5477 | 153.9093 | 153.0244 | 171.5129 | 143.0247 | 140.8235 | 126.2515
BLD11PST |  |  | Jun | 198.1387 | 180.9853 | 212.4934 | 175.4192 | 147.9208 | 199.0989 | 142.186 | 176.788 | 163.1178 | 147.2102 | 166.3798 | 156.6157 | 169.3575 | 157.9863 | 159.5742 | 136.1772
BLD11PST |  |  | Jul | 191.0273 | 189.1107 | 208.991 | 186.6656 | 151.2705 | 195.7328 | 162.2482 | 186.0853 | 172.4623 | 155.294 | 175.3684 | 164.5955 | 177.0454 | 153.1934 | 164.821 | 142.6076
BLD11PST |  |  | Aug | 191.3996 | 195.6669 | 211.9608 | 176.9845 | 152.6966 | 190.3827 | 142.9457 | 185.4951 | 170.6597 | 156.3073 | 181.5088 | 160.9536 | 176.5679 | 158.2422 | 167.6112 | 140.317
BLD11PST |  |  | Sep | 186.238 | 182.5489 | 195.1005 | 169.048 | 153.3596 | 175.558 | 154.4396 | 161.3607 | 158.737 | 161.7662 | 158.4909 | 154.4065 | 154.4598 | 155.0806 | 150.5578 | 136.1251
BLD11PST |  |  | Oct | 183.2732 | 173.4122 | 167.6939 | 158.4861 | 147.004 | 156.0072 | 142.1317 | 156.2027 | 148.2548 | 140.6754 | 147.5057 | 146.468 | 148.6069 | 139.6212 | 143.6635 | 141.74
BLD11PST |  |  | Nov | 173.5826 | 162.634 | 147.1852 | 142.1733 | 141.8626 | 137.6537 | 135.7575 | 149.911 | 137.0616 | 137.7845 | 147.6291 | 134.6679 | 135.5538 | 132.4122 | 138.1195 | 174.761
BLD11PST |  |  | Dec | 163.5197 | 162.0849 | 141.7397 | 139.6609 | 139.3351 | 132.9654 | 131.6878 | 133.5864 | 129.8543 | 128.836 | 149.8494 | 141.9746 | 170.2971 | 166.6643 | 165.8892 | 207.5568
BLD11PST |  |  | Time of Peak Electrical Demand
BLD11PST |  |  | Jan | 06-JAN-20:00 | 22-JAN-20:00 | 29-JAN-20:15 | 24-JAN-20:00 | 26-JAN-20:30 | 18-JAN-20:00 | 15-JAN-20:15 | 31-JAN-07:15 | 26-JAN-20:30 | 28-JAN-20:00 | 07-JAN-07:15 | 06-JAN-07:15 | 06-JAN-07:15 | 07-JAN-08:15 | 09-JAN-07:15 | 13-JAN-08:00
BLD11PST |  |  | Feb | 20-FEB-20:15 | 20-FEB-20:30 | 27-FEB-20:15 | 20-FEB-20:00 | 12-FEB-20:15 | 26-FEB-20:00 | 15-FEB-20:15 | 01-FEB-07:15 | 14-FEB-20:30 | 21-FEB-20:00 | 08-FEB-20:00 | 15-FEB-20:00 | 04-FEB-07:15 | 26-FEB-07:15 | 02-FEB-07:15 | 04-FEB-08:15
BLD11PST |  |  | Mar | 13-MAR-19:15 | 26-MAR-19:15 | 17-MAR-19:15 | 28-MAR-19:15 | 04-MAR-20:00 | 31-MAR-19:00 | 30-MAR-19:00 | 09-MAR-20:00 | 20-MAR-19:15 | 29-MAR-19:00 | 14-MAR-19:00 | 26-MAR-19:15 | 19-MAR-19:00 | 30-MAR-19:30 | 09-MAR-06:15 | 14-MAR-07:15
BLD11PST |  |  | Apr | 01-APR-19:15 | 30-APR-19:15 | 02-APR-19:15 | 15-APR-19:15 | 11-APR-19:15 | 21-APR-19:15 | 29-APR-19:15 | 04-APR-19:15 | 22-APR-19:15 | 29-APR-19:15 | 28-APR-19:00 | 25-APR-19:00 | 02-APR-19:00 | 30-APR-19:30 | 15-APR-19:15 | 01-APR-19:00
BLD11PST |  |  | May | 15-MAY-19:15 | 26-MAY-19:15 | 28-MAY-19:30 | 14-MAY-19:30 | 29-MAY-19:15 | 31-MAY-19:15 | 25-MAY-19:15 | 15-MAY-19:15 | 30-MAY-19:15 | 04-MAY-19:30 | 30-MAY-19:15 | 23-MAY-19:15 | 27-MAY-19:45 | 25-MAY-19:00 | 27-MAY-19:45 | 29-MAY-19:00
BLD11PST |  |  | Jun | 27-JUN-19:15 | 13-JUN-19:30 | 27-JUN-19:45 | 19-JUN-19:00 | 28-JUN-19:15 | 27-JUN-19:15 | 16-JUN-19:30 | 30-JUN-19:45 | 28-JUN-19:30 | 18-JUN-20:15 | 16-JUN-19:30 | 27-JUN-19:30 | 29-JUN-19:00 | 25-JUN-20:30 | 14-JUN-19:00 | 23-JUN-19:00
BLD11PST |  |  | Jul | 04-JUL-19:15 | 03-JUL-19:30 | 11-JUL-19:45 | 02-JUL-19:00 | 10-JUL-19:15 | 24-JUL-19:15 | 02-JUL-19:30 | 24-JUL-19:30 | 30-JUL-19:15 | 24-JUL-19:00 | 02-JUL-19:30 | 17-JUL-19:30 | 13-JUL-19:00 | 21-JUL-20:15 | 06-JUL-19:00 | 29-JUL-19:45
BLD11PST |  |  | Aug | 21-AUG-19:15 | 06-AUG-19:15 | 01-AUG-19:30 | 14-AUG-19:30 | 16-AUG-19:15 | 06-AUG-19:15 | 27-AUG-19:15 | 17-AUG-19:15 | 01-AUG-19:15 | 06-AUG-19:45 | 04-AUG-19:15 | 29-AUG-19:15 | 27-AUG-19:15 | 11-AUG-19:45 | 13-AUG-19:30 | 19-AUG-20:00
BLD11PST |  |  | Sep | 10-SEP-19:15 | 04-SEP-19:15 | 09-SEP-19:15 | 10-SEP-19:15 | 24-SEP-19:00 | 01-SEP-19:00 | 28-SEP-19:00 | 09-SEP-19:15 | 02-SEP-19:15 | 02-SEP-19:15 | 06-SEP-19:15 | 01-SEP-19:30 | 13-SEP-19:15 | 02-SEP-19:15 | 08-SEP-19:15 | 09-SEP-19:45
BLD11PST |  |  | Oct | 06-OCT-19:15 | 29-OCT-19:00 | 02-OCT-19:30 | 21-OCT-19:15 | 05-OCT-19:15 | 06-OCT-19:00 | 16-OCT-19:15 | 20-OCT-19:30 | 01-OCT-19:15 | 09-OCT-19:15 | 31-OCT-19:15 | 01-OCT-19:15 | 08-OCT-19:15 | 06-OCT-19:15 | 07-OCT-19:15 | 22-OCT-07:15
BLD11PST |  |  | Nov | 01-NOV-19:15 | 26-NOV-20:00 | 05-NOV-19:15 | 22-NOV-20:00 | 09-NOV-20:45 | 09-NOV-20:00 | 12-NOV-20:45 | 04-NOV-19:15 | 09-NOV-20:00 | 04-NOV-19:15 | 02-NOV-19:00 | 04-NOV-19:15 | 02-NOV-19:00 | 21-NOV-20:00 | 25-NOV-07:15 | 23-NOV-08:15
BLD11PST |  |  | Dec | 17-DEC-20:15 | 02-DEC-20:15 | 13-DEC-20:30 | 04-DEC-20:00 | 18-DEC-20:30 | 05-DEC-20:30 | 03-DEC-20:00 | 21-DEC-07:15 | 08-DEC-20:00 | 31-DEC-20:00 | 31-DEC-20:00 | 12-DEC-07:15 | 31-DEC-07:15 | 11-DEC-07:15 | 31-DEC-07:15 | 29-DEC-08:00
BLD11PST |  | Source Energy
BLD11PST |  |  | Total Source Energy (GJ) | 12221.87 | 12039.4 | 10710.81 | 10524.17 | 9107.49 | 11245.62 | 8669.53 | 10966.44 | 9970.52 | 5387.85 | 10965.34 | 9902.03 | 11036.83 | 10454.47 | 10984.37 | 13003.57
BLD11PST |  |  | Total Source Energy (MJ/m2) | 3045.12 | 2999.66 | 2668.64 | 2622.14 | 2269.17 | 2801.89 | 2160.05 | 2732.33 | 2484.19 | 1342.4 | 2732.06 | 2467.13 | 2749.87 | 2604.77 | 2736.8 | 3239.89
BLD11PST |  | Water Consumption (m3)
BLD11PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Water Systems | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13
BLD11PST |  |  | Total Building | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13
BLD11PST |  | Emissions
BLD11PST |  |  | Carbon Equivalent (kg) | 277507.1702 | 301163.5083 | 277921.6258 | 260336.796 | 99534.2154 | 287693.0113 | 96022.9265 | 225289.5223 | 325191.6483 | 67537.8291 | 427143.306 | 319843.2227 | 289581.0884 | 289025.1452 | 285569.7727 | 272345.6636
BLD11PST |  |  | CO2 (kg) | 647263.3201 | 759870.3718 | 658943.7782 | 599292.3955 | 268149.3556 | 687488.5268 | 259425.58 | 516233.2918 | 765970.3724 | 169028.1673 | 997263.9872 | 755077.3592 | 681208.9633 | 684168.5268 | 674174.6898 | 696647.9282
BLD11PST |  |  | NOX (kg) | 1121.344 | 985.9037 | 1091.1998 | 1117.0047 | 231.1289 | 1102.7173 | 224.1098 | 978.4465 | 1307.8626 | 237.8079 | 1762.7472 | 1281.8841 | 1181.3182 | 1161.3852 | 1158.4377 | 835.3664
BLD11PST |  |  | SO2 (kg) | 4204.0133 | 4150.1023 | 3569.5292 | 2811.6039 | 2204.9688 | 4501.7383 | 2043.7161 | 2817.4034 | 3318.8916 | 539.4462 | 5144.7828 | 3231.7536 | 1836.2983 | 1957.3311 | 1782.5542 | 4248.495
BLD11PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11PST |  |  | Hg (kg) | 0.0192 | 0.0117 | 0.0097 | 0.0103 | 0.0011 | 0.0085 | 0.001 | 0.0114 | 0.013 | 0.0022 | 0.0156 | 0.0127 | 0.0135 | 0.0137 | 0.0132 | 0.0146
BLD11PST |  |  | Water for Electricity (m3) | 520.2891 | 1415.61 | 26366.8 | 5000.93 | 13303.4 | 22450.5 | 12330.2 | 175.2134 | 3450.91 | 7127.35 | 1184.32 | 3360.25 | 1206.85 | 46427 | 1171.49 | 852.5916
BLD11PST |  | Program
BLD11NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD11NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD11NEW |  |  | Weighting Factor | 3.1231 | 88.1153 | 9.1306 | 82.0032 |  | 34.8301 | 6.663 | 96.3435 | 6.2231 | 12.0231 | 111.6509 | 27.3736 | 32.6486 | 9.4333 | 6.2759 | 1.1875
BLD11NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD11NEW |  |  | Exterior walls
BLD11NEW | TypeWall |  | Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
BLD11NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 3.2051
BLD11NEW |  |  | Roof
BLD11NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD11NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD11NEW |  |  | Window
BLD11NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD11NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD11NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BLD11NEW |  |  | Skylights/TDD
BLD11NEW |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD11NEW |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD11NEW |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD11NEW |  |  | Foundation
BLD11NEW |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD11NEW |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD11NEW |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD11NEW |  | HVAC
BLD11NEW |  |  | HVAC Sizing
BLD11NEW | HVAC |  | Air Conditioning (kW) | 276.3634 | 279.8684 | 281.0555 | 262.8575 | 228.8239 | 258.8043 | 238.8149 | 258.3681 | 260.1166 | 227.5111 | 258.1337 | 256.5367 | 252.0397 | 244.8212 | 240.6974 | 205.7895
BLD11NEW |  |  | GUESTROOM101 PTAC DXCOIL | 1.8363 | 1.9103 | 1.8261 | 1.7313 | 1.4454 | 1.5155 | 1.7606 | 1.683 | 1.5124 | 1.4229 | 1.6811 | 1.5186 | 1.6319 | 1.4758 | 1.4193 | 1.2153
BLD11NEW |  |  | GUESTROOM102 PTAC DXCOIL | 1.8583 | 1.9334 | 1.8534 | 1.7526 | 1.4682 | 1.5376 | 1.8078 | 1.7033 | 1.5355 | 1.4533 | 1.7015 | 1.5411 | 1.6527 | 1.5005 | 1.4419 | 1.2404
BLD11NEW |  |  | GUESTROOM103 PTAC DXCOIL | 2.0066 | 2.0861 | 2.0259 | 1.8687 | 1.5588 | 1.6376 | 1.8203 | 1.7922 | 1.5945 | 1.4963 | 1.7855 | 1.5873 | 1.7273 | 1.5535 | 1.471 | 1.2467
BLD11NEW |  |  | GUESTROOM104 PTAC DXCOIL | 1.9201 | 1.8884 | 1.7387 | 1.6584 | 1.3409 | 1.4427 | 1.0987 | 1.5902 | 1.4614 | 1.1742 | 1.5705 | 1.4169 | 1.5115 | 1.3416 | 1.2355 | 0.96982
BLD11NEW |  |  | GUESTROOM105 PTAC DXCOIL | 1.9204 | 1.8775 | 1.7113 | 1.6901 | 1.4339 | 1.4903 | 1.2402 | 1.6394 | 1.6131 | 1.2934 | 1.6257 | 1.5859 | 1.5706 | 1.4956 | 1.3733 | 1.1365
BLD11NEW |  |  | GUESTROOM201 PTAC DXCOIL | 2.6719 | 2.7281 | 2.8819 | 2.3362 | 2.1232 | 2.501 | 2.4259 | 2.1636 | 2.3282 | 2.0555 | 2.182 | 2.3072 | 2.1267 | 2.2443 | 2.1166 | 1.8852
BLD11NEW |  |  | GUESTROOM202_205 PTAC DXCOIL | 7.9654 | 8.3008 | 8.5772 | 7.7307 | 6.7783 | 7.5488 | 9.0035 | 7.632 | 7.7995 | 7.4296 | 7.6953 | 7.8422 | 7.5234 | 7.6745 | 7.4389 | 7.14
BLD11NEW |  |  | GUESTROOM206_208 PTAC DXCOIL | 6.3114 | 6.5799 | 6.8457 | 6.1504 | 5.4308 | 6.0778 | 7.6473 | 6.057 | 6.2686 | 6.1114 | 6.1255 | 6.3018 | 6.0668 | 6.2202 | 6.0923 | 5.8678
BLD11NEW |  |  | GUESTROOM209_212 PTAC DXCOIL | 7.8086 | 8.1285 | 8.3851 | 7.5655 | 6.573 | 7.3232 | 8.7756 | 7.46 | 7.5599 | 7.1983 | 7.5202 | 7.6009 | 7.3467 | 7.4372 | 7.1997 | 6.9121
BLD11NEW |  |  | GUESTROOM213 PTAC DXCOIL | 2.2018 | 2.2912 | 2.4091 | 2.1133 | 1.8616 | 2.1371 | 2.3843 | 2.0675 | 2.1123 | 2.0032 | 2.0799 | 2.1057 | 2.0251 | 2.0704 | 2.0007 | 1.8997
BLD11NEW |  |  | GUESTROOM214 PTAC DXCOIL | 2.1408 | 2.1231 | 2.1698 | 1.9358 | 1.675 | 2.0358 | 1.6144 | 1.8814 | 2.0109 | 1.67 | 1.8821 | 1.9674 | 1.8372 | 1.89 | 1.7875 | 1.6014
BLD11NEW |  |  | GUESTROOM215_218 PTAC DXCOIL | 8.142 | 8.072 | 7.9827 | 7.6953 | 6.6771 | 7.6761 | 6.6265 | 7.7335 | 8.0886 | 6.7119 | 7.7513 | 8.003 | 7.5484 | 7.6234 | 7.1162 | 6.5538
BLD11NEW |  |  | GUESTROOM219 PTAC DXCOIL | 2.4202 | 2.3902 | 2.5006 | 2.3849 | 2.1651 | 2.4617 | 2.1457 | 2.3579 | 2.6179 | 2.1764 | 2.3644 | 2.596 | 2.3086 | 2.4739 | 2.2964 | 2.1665
BLD11NEW |  |  | GUESTROOM220_223 PTAC DXCOIL | 7.6152 | 7.5431 | 7.4271 | 7.1466 | 5.9862 | 6.9145 | 5.9113 | 7.0201 | 7.2467 | 6.0029 | 7.1951 | 7.1593 | 6.9951 | 6.8169 | 6.3849 | 5.8242
BLD11NEW |  |  | GUESTROOM224 PTAC DXCOIL | 2.1194 | 2.0867 | 2.1121 | 1.9102 | 1.6784 | 1.9974 | 1.6292 | 1.9349 | 2.0232 | 1.6817 | 1.8786 | 1.9836 | 1.8219 | 1.896 | 1.7826 | 1.6093
BLD11NEW |  |  | GUESTROOM301 PTAC DXCOIL | 2.6636 | 2.7075 | 2.8925 | 2.3326 | 2.1042 | 2.5109 | 2.4036 | 2.1562 | 2.3188 | 2.0442 | 2.1729 | 2.2916 | 2.1113 | 2.2308 | 2.1056 | 1.8868
BLD11NEW |  |  | GUESTROOM302_305 PTAC DXCOIL | 7.9595 | 8.2961 | 8.6319 | 7.7541 | 6.7745 | 7.6506 | 9.0426 | 7.6498 | 7.8421 | 7.4506 | 7.7144 | 7.875 | 7.5098 | 7.7093 | 7.4686 | 7.2292
BLD11NEW |  |  | GUESTROOM306_308 PTAC DXCOIL | 6.3979 | 6.6796 | 7.0081 | 6.2585 | 5.5599 | 6.3046 | 7.8629 | 6.1814 | 6.4505 | 6.283 | 6.2358 | 6.4791 | 6.1057 | 6.388 | 6.2727 | 6.0907
BLD11NEW |  |  | GUESTROOM309_312 PTAC DXCOIL | 7.9466 | 8.2839 | 8.6194 | 7.7446 | 6.7611 | 7.6373 | 9.0324 | 7.6421 | 7.8306 | 7.4407 | 7.7062 | 7.8632 | 7.5288 | 7.6965 | 7.458 | 7.2183
BLD11NEW |  |  | GUESTROOM313 PTAC DXCOIL | 2.2479 | 2.3393 | 2.4877 | 2.1701 | 1.9162 | 2.2423 | 2.4534 | 2.1188 | 2.1968 | 2.0787 | 2.1394 | 2.1836 | 2.082 | 2.1509 | 2.0809 | 1.9965
BLD11NEW |  |  | GUESTROOM314 PTAC DXCOIL | 2.1873 | 2.1607 | 2.2717 | 1.9973 | 1.7206 | 2.1453 | 1.675 | 1.9293 | 2.0954 | 1.738 | 1.9398 | 2.044 | 1.912 | 1.9697 | 1.8716 | 1.6917
BLD11NEW |  |  | GUESTROOM315_318 PTAC DXCOIL | 7.87 | 7.8067 | 7.7725 | 7.1789 | 6.2962 | 7.3904 | 6.2851 | 7.2949 | 7.6805 | 6.3683 | 7.1003 | 7.5825 | 6.8735 | 7.2364 | 6.8031 | 6.2607
BLD11NEW |  |  | GUESTROOM319 PTAC DXCOIL | 2.0731 | 2.0567 | 2.0577 | 1.8921 | 1.686 | 1.9857 | 1.6792 | 1.9206 | 2.0568 | 1.7052 | 1.8691 | 2.028 | 1.8116 | 1.9361 | 1.8194 | 1.6716
BLD11NEW |  |  | GUESTROOM320_323 PTAC DXCOIL | 7.7727 | 7.7094 | 7.6697 | 7.0822 | 6.1753 | 7.2534 | 6.1656 | 7.2 | 7.5343 | 6.2479 | 7.0063 | 7.4369 | 6.7803 | 7.098 | 6.6759 | 6.1362
BLD11NEW |  |  | GUESTROOM324 PTAC DXCOIL | 2.1686 | 2.1385 | 2.2191 | 1.9728 | 1.727 | 2.1107 | 1.6932 | 1.9274 | 2.104 | 1.751 | 1.9275 | 2.0563 | 1.8971 | 1.9724 | 1.8644 | 1.698
BLD11NEW |  |  | GUESTROOM401 PTAC DXCOIL | 3.2817 | 3.3725 | 3.6495 | 2.9445 | 2.545 | 3.1564 | 2.7124 | 2.6875 | 2.8618 | 2.4275 | 2.6664 | 2.7544 | 2.5509 | 2.6548 | 2.4942 | 2.0484
BLD11NEW |  |  | GUESTROOM402_405 PTAC DXCOIL | 10.0147 | 10.4447 | 10.7895 | 9.794 | 8.3868 | 10.0359 | 10.0308 | 9.6013 | 9.9757 | 8.6787 | 9.5647 | 9.6714 | 9.2342 | 9.4212 | 8.8647 | 7.5652
BLD11NEW |  |  | GUESTROOM406_408 PTAC DXCOIL | 8.0831 | 8.4195 | 8.7812 | 7.9148 | 6.8742 | 8.242 | 8.6774 | 7.7949 | 8.1798 | 7.2568 | 7.7699 | 7.9347 | 7.4893 | 7.7506 | 7.3595 | 6.3736
BLD11NEW |  |  | GUESTROOM409_412 PTAC DXCOIL | 10.0284 | 10.4383 | 10.7838 | 9.7957 | 8.3885 | 10.039 | 10.0373 | 9.6078 | 9.982 | 8.688 | 9.6045 | 9.6779 | 9.2411 | 9.4281 | 8.8724 | 7.5736
BLD11NEW |  |  | GUESTROOM413 PTAC DXCOIL | 2.8172 | 2.9332 | 3.1152 | 2.7489 | 2.3802 | 2.9326 | 2.7224 | 2.6654 | 2.8126 | 2.4452 | 2.6495 | 2.7007 | 2.5553 | 2.6426 | 2.4914 | 2.0896
BLD11NEW |  |  | GUESTROOM414 PTAC DXCOIL | 2.8046 | 2.8338 | 3.0421 | 2.6588 | 2.1876 | 2.8368 | 1.9941 | 2.5769 | 2.6979 | 2.1847 | 2.5399 | 2.5493 | 2.4261 | 2.4461 | 2.2897 | 1.8667
BLD11NEW |  |  | GUESTROOM415_418 PTAC DXCOIL | 10.0864 | 10.1356 | 10.2431 | 9.6102 | 7.9041 | 9.8056 | 7.384 | 9.3594 | 9.8066 | 7.8958 | 9.2456 | 9.3867 | 8.8445 | 8.9394 | 8.3201 | 6.8264
BLD11NEW |  |  | GUESTROOM419 PTAC DXCOIL | 2.6242 | 2.6491 | 2.7283 | 2.4967 | 2.0731 | 2.5907 | 1.9182 | 2.4345 | 2.5728 | 2.0666 | 2.401 | 2.4533 | 2.2947 | 2.3389 | 2.1784 | 1.7613
BLD11NEW |  |  | GUESTROOM420_423 PTAC DXCOIL | 10.0257 | 10.0747 | 10.1605 | 9.549 | 7.8335 | 9.7225 | 7.3185 | 9.3026 | 9.7223 | 7.828 | 9.1891 | 9.3044 | 8.7892 | 8.8615 | 8.2496 | 6.7586
BLD11NEW |  |  | GUESTROOM424 PTAC DXCOIL | 2.7892 | 2.7994 | 2.9899 | 2.638 | 2.1936 | 2.803 | 2.0113 | 2.5632 | 2.7087 | 2.1921 | 2.5331 | 2.5682 | 2.422 | 2.4566 | 2.3004 | 1.8736
BLD11NEW |  |  | PSZ-HEATCOOL:1_COOLC DXCOIL | 8.6251 | 8.5489 | 8.2503 | 8.4013 | 7.516 | 7.6446 | 6.6094 | 8.0608 | 8.7281 | 7.2336 | 8.047 | 8.653 | 8.1285 | 8.2899 | 7.5967 | 6.2016
BLD11NEW |  |  | PSZ-HEATCOOL:10_COOLC DXCOIL | 4.6633 | 4.6827 | 4.6502 | 4.2519 | 3.5432 | 4.1264 | 3.8018 | 4.2827 | 4.2761 | 3.6576 | 4.295 | 4.2135 | 4.1595 | 4.053 | 3.8786 | 3.3393
BLD11NEW |  |  | PSZ-HEATCOOL:11_COOLC DXCOIL | 4.3703 | 4.3865 | 4.4223 | 3.9652 | 3.1768 | 3.8659 | 3.4576 | 3.9969 | 3.8852 | 3.3304 | 4.007 | 3.8009 | 3.8698 | 3.6757 | 3.5581 | 3.0668
BLD11NEW |  |  | PSZ-HEATCOOL:12_COOLC DXCOIL | 6.8909 | 7.0764 | 7.1462 | 6.4622 | 4.8895 | 6.4229 | 4.6351 | 6.3291 | 6.1339 | 4.9477 | 6.1914 | 5.7012 | 5.8567 | 5.4885 | 5.2616 | 4.5296
BLD11NEW |  |  | PSZ-HEATCOOL:2_COOLC DXCOIL | 18.8712 | 19.4209 | 20.0523 | 18.6806 | 17.4092 | 18.5742 | 15.4603 | 17.9489 | 15.7173 | 15.2831 | 18.1647 | 15.7223 | 18.2918 | 14.3925 | 18.6088 | 11.5185
BLD11NEW |  |  | PSZ-HEATCOOL:3_COOLC DXCOIL | 1.2675 | 1.3148 | 1.2763 | 1.2602 | 1.2181 | 1.1669 | 1.1723 | 1.1808 | 1.2423 | 1.1193 | 1.1867 | 1.2459 | 1.1963 | 1.2134 | 1.1022 | 0.93911
BLD11NEW |  |  | PSZ-HEATCOOL:4_COOLC DXCOIL | 10.6599 | 10.6599 | 10.6599 | 10.6599 | 10.6599 | 10.6599 | 8.5734 | 10.6599 | 10.4175 | 9.7293 | 10.6599 | 10.5457 | 10.6599 | 8.7987 | 10.6599 | 7.106
BLD11NEW |  |  | PSZ-HEATCOOL:5_COOLC DXCOIL | 1.1609 | 1.2054 | 1.0665 | 1.0638 | 0.88538 | 0.84158 | 0.84316 | 1.019 | 0.82966 | 0.77202 | 1.0137 | 0.83504 | 0.98451 | 0.82227 | 0.793 | 0.59058
BLD11NEW |  |  | PSZ-HEATCOOL:6_COOLC DXCOIL | 7.9091 | 7.7664 | 6.9706 | 7.181 | 5.9031 | 6.0839 | 4.8808 | 7.1514 | 5.9647 | 5.2328 | 7.1457 | 5.9474 | 6.8575 | 5.6248 | 5.8855 | 4.738
BLD11NEW |  |  | PSZ-HEATCOOL:7_COOLC DXCOIL | 28.7679 | 28.3953 | 27.2935 | 27.6728 | 24.9543 | 26.5097 | 23.9408 | 27.4193 | 29.7558 | 24.6872 | 27.4435 | 29.6982 | 27.036 | 28.0584 | 25.6363 | 24.1764
BLD11NEW |  |  | PSZ-HEATCOOL:8_COOLC DXCOIL | 3.2244 | 3.2234 | 3.1827 | 3.19 | 2.8815 | 3.0283 | 2.0449 | 3.0191 | 2.2934 | 1.9042 | 3.0282 | 2.2618 | 3.0611 | 2.127 | 2.9169 | 1.8209
BLD11NEW |  |  | PSZ-HEATCOOL:9_COOLC DXCOIL | 9.1724 | 8.9693 | 7.7246 | 7.8653 | 6.1036 | 6.1874 | 4.4048 | 7.9706 | 5.6701 | 4.9621 | 7.9367 | 5.5535 | 7.7848 | 5.2355 | 5.8024 | 3.8769
BLD11NEW | HEAT |  | Heating (kW) | 248.7838 | 286.9997 | 254.3215 | 291.5743 | 232.3817 | 255.473 | 245.0928 | 308.2999 | 270.3047 | 268.9622 | 340.2691 | 299.2654 | 330.22 | 311.7547 | 337.6035 | 392.1863
BLD11NEW |  |  | FRONTSTAIRSFLR1 UNIT HEATER COIL | 0 | 0.19853 | 0.04015 | 0.24181 | 0 | 0.09968 | 0 | 0.29361 | 0.18538 | 0.07983 | 0.6117 | 0.46157 | 0.79723 | 0.76652 | 0.89004 | 1.3394
BLD11NEW |  |  | FRONTSTAIRSFLR2 UNIT HEATER COIL | 0 | 0.33201 | 0.14759 | 0.33778 | 0 | 0.17217 | 0 | 0.36755 | 0.25621 | 0.18688 | 0.62667 | 0.49112 | 0.78008 | 0.75111 | 0.85455 | 1.2026
BLD11NEW |  |  | FRONTSTAIRSFLR3 UNIT HEATER COIL | 0 | 0.37765 | 0.18416 | 0.382 | 0 | 0.21149 | 0.08014 | 0.41454 | 0.30136 | 0.23537 | 0.67639 | 0.54011 | 0.82928 | 0.80121 | 0.90442 | 1.2497
BLD11NEW |  |  | FRONTSTAIRSFLR4 UNIT HEATER COIL | 0.15676 | 0.73912 | 0.45127 | 0.80975 | 0.17283 | 0.54498 | 0.34958 | 0.92103 | 0.73344 | 0.62529 | 1.3396 | 1.1239 | 1.5926 | 1.559 | 1.7182 | 2.2616
BLD11NEW |  |  | FRONTSTORAGEFLR1 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | FRONTSTORAGEFLR2 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | FRONTSTORAGEFLR3 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | FRONTSTORAGEFLR4 UNIT HEATER COIL | 0 | 0.03312 | 0 | 0.04884 | 0 | 0 | 0 | 0.08035 | 0.04111 | 0 | 0.18922 | 0.14822 | 0.25687 | 0.26342 | 0.293 | 0.39307
BLD11NEW |  |  | GUESTROOM101 PTAC HEAT COIL | 0.55632 | 0.8082 | 0.68417 | 0.86317 | 0.5786 | 0.74686 | 0.63954 | 0.96638 | 0.83431 | 0.76451 | 1.256 | 1.0812 | 1.4227 | 1.3648 | 1.5016 | 1.9055
BLD11NEW |  |  | GUESTROOM102 PTAC HEAT COIL | 0.55632 | 0.82977 | 0.70314 | 0.88373 | 0.5786 | 0.76542 | 0.63954 | 0.98731 | 0.85488 | 0.783 | 1.2786 | 1.1033 | 1.4462 | 1.3884 | 1.5256 | 1.9296
BLD11NEW |  |  | GUESTROOM103 PTAC HEAT COIL | 0.55632 | 1.0449 | 0.89946 | 1.0955 | 0.5786 | 0.9637 | 0.76486 | 1.195 | 1.0616 | 0.96383 | 1.4977 | 1.3212 | 1.6722 | 1.6165 | 1.7551 | 2.1669
BLD11NEW |  |  | GUESTROOM104 PTAC HEAT COIL | 0.55632 | 1.0341 | 0.89365 | 1.0937 | 0.5786 | 0.97229 | 0.75963 | 1.1947 | 1.0598 | 0.9794 | 1.4951 | 1.3199 | 1.6664 | 1.6107 | 1.7487 | 2.1654
BLD11NEW |  |  | GUESTROOM105 PTAC HEAT COIL | 0.55632 | 0.82056 | 0.69759 | 0.88258 | 0.5786 | 0.76651 | 0.63954 | 0.98754 | 0.85349 | 0.7817 | 1.2804 | 1.106 | 1.4474 | 1.3899 | 1.5272 | 1.9375
BLD11NEW |  |  | GUESTROOM201 PTAC HEAT COIL | 0.6985 | 1.2969 | 0.99563 | 1.2769 | 0.64977 | 1.0065 | 0.86161 | 1.3552 | 1.141 | 1.0697 | 1.7592 | 1.5065 | 1.9856 | 1.9051 | 2.0919 | 2.5763
BLD11NEW |  |  | GUESTROOM202_205 PTAC HEAT COIL | 2.2253 | 3.2574 | 2.4936 | 3.3357 | 2.3144 | 2.6793 | 2.5582 | 3.687 | 3.0544 | 3.0508 | 4.7732 | 4.0159 | 5.3714 | 5.0888 | 5.6448 | 6.9998
BLD11NEW |  |  | GUESTROOM206_208 PTAC HEAT COIL | 1.669 | 2.5087 | 1.9001 | 2.5412 | 1.7358 | 2.0095 | 1.9186 | 2.8257 | 2.3356 | 2.2881 | 3.6949 | 3.104 | 4.1706 | 3.953 | 4.3914 | 5.427
BLD11NEW |  |  | GUESTROOM209_212 PTAC HEAT COIL | 2.2253 | 3.1823 | 2.4785 | 3.273 | 2.3144 | 2.6793 | 2.5582 | 3.6244 | 2.9958 | 3.0508 | 4.6952 | 3.941 | 5.2847 | 5.0003 | 5.553 | 6.9034
BLD11NEW |  |  | GUESTROOM213 PTAC HEAT COIL | 0.5845 | 1.0392 | 0.83709 | 1.0552 | 0.5786 | 0.86662 | 0.75942 | 1.1378 | 0.97741 | 0.93546 | 1.4184 | 1.2276 | 1.5724 | 1.503 | 1.6429 | 1.9869
BLD11NEW |  |  | GUESTROOM214 PTAC HEAT COIL | 0.55632 | 1.0071 | 0.80955 | 1.0252 | 0.5786 | 0.83975 | 0.72383 | 1.1092 | 0.94775 | 0.90833 | 1.389 | 1.1998 | 1.5422 | 1.4727 | 1.6138 | 1.9601
BLD11NEW |  |  | GUESTROOM215_218 PTAC HEAT COIL | 2.2253 | 2.9377 | 2.4785 | 3.169 | 2.3144 | 2.6793 | 2.5582 | 3.5277 | 2.8029 | 3.0508 | 4.4101 | 3.6574 | 5.0048 | 4.7189 | 5.2796 | 6.6534
BLD11NEW |  |  | GUESTROOM219 PTAC HEAT COIL | 0.6954 | 0.73442 | 0.66806 | 0.79225 | 0.69293 | 0.64253 | 0.69515 | 0.88192 | 0.57203 | 0.68556 | 1.0303 | 0.83647 | 1.1134 | 1.0146 | 1.1397 | 1.4631
BLD11NEW |  |  | GUESTROOM220_223 PTAC HEAT COIL | 2.2253 | 3.0526 | 2.4785 | 3.169 | 2.3144 | 2.6793 | 2.5582 | 3.5277 | 2.8727 | 3.0508 | 4.5861 | 3.8373 | 5.1752 | 4.8895 | 5.4479 | 6.8131
BLD11NEW |  |  | GUESTROOM224 PTAC HEAT COIL | 0.55632 | 0.92942 | 0.73225 | 0.94866 | 0.5786 | 0.76235 | 0.66973 | 1.0339 | 0.87179 | 0.83079 | 1.3211 | 1.1289 | 1.4781 | 1.4078 | 1.5514 | 1.9066
BLD11NEW |  |  | GUESTROOM301 PTAC HEAT COIL | 0.75786 | 1.3466 | 1.0318 | 1.3251 | 0.69324 | 1.0427 | 0.90081 | 1.4042 | 1.1844 | 1.1135 | 1.8147 | 1.5586 | 2.0439 | 1.9643 | 2.1525 | 2.6314
BLD11NEW |  |  | GUESTROOM302_305 PTAC HEAT COIL | 2.2253 | 3.3885 | 2.5851 | 3.4719 | 2.3144 | 2.7168 | 2.5582 | 3.8355 | 3.1843 | 3.0508 | 4.9371 | 4.1689 | 5.5407 | 5.2603 | 5.8201 | 7.1472
BLD11NEW |  |  | GUESTROOM306_308 PTAC HEAT COIL | 1.669 | 2.7223 | 2.0734 | 2.7556 | 1.7358 | 2.1535 | 1.9511 | 3.0467 | 2.5419 | 2.4214 | 3.9311 | 3.3294 | 4.4117 | 4.1955 | 4.639 | 5.648
BLD11NEW |  |  | GUESTROOM309_312 PTAC HEAT COIL | 2.2253 | 3.3706 | 2.5733 | 3.4593 | 2.3144 | 2.7084 | 2.5582 | 3.8249 | 3.1753 | 3.0508 | 4.9209 | 4.1538 | 5.5214 | 5.2402 | 5.7992 | 7.124
BLD11NEW |  |  | GUESTROOM313 PTAC HEAT COIL | 0.66217 | 1.0834 | 0.87192 | 1.1 | 0.63012 | 0.90216 | 0.8118 | 1.1857 | 1.021 | 0.98119 | 1.4717 | 1.2778 | 1.6278 | 1.559 | 1.7002 | 2.0376
BLD11NEW |  |  | GUESTROOM314 PTAC HEAT COIL | 0.6225 | 1.0578 | 0.8496 | 1.0762 | 0.59247 | 0.87958 | 0.78158 | 1.1626 | 0.99661 | 0.95823 | 1.4484 | 1.2558 | 1.6046 | 1.535 | 1.678 | 2.0157
BLD11NEW |  |  | GUESTROOM315_318 PTAC HEAT COIL | 2.2253 | 3.3125 | 2.5271 | 3.4091 | 2.3144 | 2.6793 | 2.5582 | 3.7741 | 3.1191 | 3.0508 | 4.8749 | 4.1125 | 5.4741 | 5.1884 | 5.7549 | 7.0819
BLD11NEW |  |  | GUESTROOM319 PTAC HEAT COIL | 0.55632 | 0.80581 | 0.61963 | 0.82415 | 0.5786 | 0.66983 | 0.63954 | 0.91736 | 0.7428 | 0.76269 | 1.211 | 1.0134 | 1.3719 | 1.3007 | 1.4479 | 1.7969
BLD11NEW |  |  | GUESTROOM320_323 PTAC HEAT COIL | 2.2253 | 3.3092 | 2.5295 | 3.4106 | 2.3144 | 2.6793 | 2.5582 | 3.7746 | 3.123 | 3.0508 | 4.8698 | 4.1088 | 5.4659 | 5.1799 | 5.7451 | 7.0702
BLD11NEW |  |  | GUESTROOM324 PTAC HEAT COIL | 0.57925 | 0.99388 | 0.78262 | 1.015 | 0.5786 | 0.81478 | 0.72764 | 1.102 | 0.93533 | 0.89564 | 1.3922 | 1.1969 | 1.5507 | 1.4802 | 1.6254 | 1.97
BLD11NEW |  |  | GUESTROOM401 PTAC HEAT COIL | 1.0407 | 1.8433 | 1.4283 | 1.8938 | 1.0215 | 1.5102 | 1.2943 | 2.0666 | 1.7685 | 1.6395 | 2.6548 | 2.3209 | 3.0001 | 2.9303 | 3.1729 | 3.8163
BLD11NEW |  |  | GUESTROOM402_405 PTAC HEAT COIL | 3.0088 | 5.3305 | 4.1298 | 5.6876 | 3.0873 | 4.533 | 3.9537 | 6.4163 | 5.453 | 5.0946 | 8.2156 | 7.136 | 9.2739 | 9.0262 | 9.8046 | 11.7817
BLD11NEW |  |  | GUESTROOM406_408 PTAC HEAT COIL | 2.4344 | 4.3085 | 3.3369 | 4.5634 | 2.4745 | 3.6373 | 3.2035 | 5.1506 | 4.3927 | 4.0913 | 6.5995 | 5.7457 | 7.4475 | 7.2577 | 7.8783 | 9.4114
BLD11NEW |  |  | GUESTROOM409_412 PTAC HEAT COIL | 3.0073 | 5.3202 | 4.1242 | 5.6815 | 3.0897 | 4.5304 | 3.9539 | 6.4126 | 5.4504 | 5.0943 | 8.2073 | 7.1286 | 9.2632 | 9.015 | 9.7927 | 11.7678
BLD11NEW |  |  | GUESTROOM413 PTAC HEAT COIL | 0.97146 | 1.585 | 1.2734 | 1.6728 | 0.99077 | 1.3749 | 1.2174 | 1.8538 | 1.6104 | 1.5131 | 2.3165 | 2.0449 | 2.5888 | 2.5301 | 2.7257 | 3.2268
BLD11NEW |  |  | GUESTROOM414 PTAC HEAT COIL | 0.94862 | 1.5639 | 1.2538 | 1.6539 | 0.96824 | 1.3546 | 1.1965 | 1.8346 | 1.59 | 1.4922 | 2.2984 | 2.028 | 2.5707 | 2.5106 | 2.7084 | 3.2086
BLD11NEW |  |  | GUESTROOM415_418 PTAC HEAT COIL | 2.9947 | 5.3055 | 4.1218 | 5.6793 | 3.0789 | 4.526 | 3.9501 | 6.4099 | 5.4437 | 5.0882 | 8.2075 | 7.1335 | 9.263 | 9.0088 | 9.7955 | 11.7695
BLD11NEW |  |  | GUESTROOM419 PTAC HEAT COIL | 0.78616 | 1.4227 | 1.1013 | 1.5215 | 0.80874 | 1.2087 | 1.046 | 1.7161 | 1.4601 | 1.3549 | 2.2052 | 1.9225 | 2.4942 | 2.4342 | 2.641 | 3.1695
BLD11NEW |  |  | GUESTROOM420_423 PTAC HEAT COIL | 2.9732 | 5.2762 | 4.0964 | 5.6521 | 3.06 | 4.5024 | 3.9271 | 6.3819 | 5.4176 | 5.0649 | 8.1739 | 7.1013 | 9.2265 | 8.9718 | 9.7574 | 11.7287
BLD11NEW |  |  | GUESTROOM424 PTAC HEAT COIL | 0.89889 | 1.5348 | 1.2203 | 1.6297 | 0.92431 | 1.3301 | 1.162 | 1.8124 | 1.57 | 1.4757 | 2.2695 | 1.9999 | 2.5381 | 2.4767 | 2.6738 | 3.1709
BLD11NEW |  |  | REARSTAIRSFLR1 UNIT HEATER COIL | 0 | 0.11068 | 0 | 0.144 | 0 | 0 | 0 | 0.19641 | 0.08854 | 0 | 0.50097 | 0.35578 | 0.68099 | 0.65162 | 0.77008 | 1.2029
BLD11NEW |  |  | REARSTAIRSFLR2 UNIT HEATER COIL | 0 | 0.2199 | 0.03507 | 0.22202 | 0 | 0.05981 | 0 | 0.25207 | 0.1426 | 0.07676 | 0.50341 | 0.37234 | 0.64783 | 0.61691 | 0.71685 | 1.0509
BLD11NEW |  |  | REARSTAIRSFLR3 UNIT HEATER COIL | 0 | 0.24903 | 0.06412 | 0.25309 | 0 | 0.08531 | 0 | 0.28561 | 0.17302 | 0.10893 | 0.53748 | 0.40545 | 0.68241 | 0.65296 | 0.75382 | 1.087
BLD11NEW |  |  | REARSTAIRSFLR4 UNIT HEATER COIL | 0 | 0.57757 | 0.30765 | 0.64598 | 0.0278 | 0.39156 | 0.20338 | 0.75698 | 0.57141 | 0.4689 | 1.1687 | 0.95428 | 1.4179 | 1.3822 | 1.5418 | 2.0793
BLD11NEW |  |  | REARSTORAGEFLR1 UNIT HEATER COIL | 0 | 0.0618 | 0 | 0.05789 | 0 | 0 | 0 | 0.06814 | 0 | 0 | 0.28193 | 0.20554 | 0.40593 | 0.4041 | 0.47154 | 0.73625
BLD11NEW |  |  | REARSTORAGEFLR2 UNIT HEATER COIL | 0 | 0.20124 | 0.0631 | 0.17547 | 0 | 0.05944 | 0 | 0.17431 | 0.11215 | 0.04574 | 0.34801 | 0.27342 | 0.45109 | 0.44409 | 0.50305 | 0.69942
BLD11NEW |  |  | REARSTORAGEFLR3 UNIT HEATER COIL | 0 | 0.23233 | 0.0905 | 0.20614 | 0 | 0.08792 | 0 | 0.2061 | 0.14122 | 0.08547 | 0.38472 | 0.30886 | 0.48909 | 0.48298 | 0.54206 | 0.73649
BLD11NEW |  |  | REARSTORAGEFLR4 UNIT HEATER COIL | 0.05392 | 0.48014 | 0.27713 | 0.49701 | 0.05011 | 0.31546 | 0.17737 | 0.55114 | 0.44226 | 0.34528 | 0.83933 | 0.72047 | 1.0143 | 1.0168 | 1.1051 | 1.4068
BLD11NEW |  |  | PSZ-HEATCOOL:1_HEATC | 24.5027 | 24.9523 | 23.0449 | 23.9838 | 21.5959 | 20.7213 | 19.1703 | 23.9387 | 21.3268 | 21.0503 | 12.7807 | 11.3468 | 13.0307 | 11.8904 | 12.186 | 11.3192
BLD11NEW |  |  | PSZ-HEATCOOL:10_HEATC | 11.5444 | 6.5641 | 6.5834 | 6.2974 | 10.0725 | 6.0902 | 10.9894 | 6.4968 | 5.8208 | 5.9611 | 6.8087 | 6.0378 | 6.9675 | 6.4697 | 6.9192 | 6.9333
BLD11NEW |  |  | PSZ-HEATCOOL:11_HEATC | 5.6584 | 6.1065 | 6.25 | 5.8631 | 4.9403 | 5.7561 | 5.4749 | 6.0533 | 5.3743 | 5.5132 | 6.3644 | 5.5674 | 6.5168 | 6.0153 | 6.4965 | 6.561
BLD11NEW |  |  | PSZ-HEATCOOL:12_HEATC | 8.8304 | 9.5697 | 10.073 | 9.1376 | 7.3102 | 9.0373 | 7.1097 | 9.1003 | 7.9435 | 7.7277 | 9.151 | 7.7346 | 9.0352 | 8.1989 | 8.7446 | 8.5604
BLD11NEW |  |  | PSZ-HEATCOOL:2_HEATC | 24.1307 | 29.8589 | 26.7431 | 30.632 | 23.8699 | 26.6345 | 28.3501 | 32.8372 | 27.7586 | 29.9799 | 37.2896 | 31.757 | 39.8012 | 36.9775 | 40.7075 | 47.4933
BLD11NEW |  |  | PSZ-HEATCOOL:3_HEATC | 3.7057 | 1.8191 | 1.7028 | 1.686 | 1.6856 | 1.4973 | 1.6274 | 1.6311 | 1.4191 | 1.5324 | 1.6117 | 1.4207 | 1.6122 | 1.4612 | 1.4543 | 1.2833
BLD11NEW |  |  | PSZ-HEATCOOL:4_HEATC | 16.6197 | 21.9403 | 18.5109 | 23.6679 | 17.2852 | 20.0108 | 19.1482 | 26.3467 | 21.2855 | 22.7848 | 30.7783 | 25.3463 | 33.2623 | 30.3803 | 34.0465 | 42.1613
BLD11NEW |  |  | PSZ-HEATCOOL:5_HEATC | 1.4185 | 1.5809 | 1.4038 | 1.4899 | 1.3667 | 1.2392 | 1.346 | 1.4727 | 1.1912 | 1.3049 | 1.5416 | 1.2729 | 1.5898 | 1.4034 | 1.4486 | 1.4233
BLD11NEW |  |  | PSZ-HEATCOOL:6_HEATC | 14.5799 | 9.7835 | 8.9596 | 10.002 | 8.4653 | 9.0855 | 8.5107 | 10.4289 | 9.4411 | 9.3914 | 11.3362 | 10.2432 | 11.8396 | 11.2329 | 11.8439 | 13.1269
BLD11NEW |  |  | PSZ-HEATCOOL:7_HEATC | 73.0416 | 74.3716 | 72.1225 | 74.5416 | 71.5579 | 71.8808 | 69.4136 | 75.0961 | 72.8391 | 71.9204 | 76.4312 | 73.9303 | 42.4588 | 41.0359 | 42.0433 | 43.8491
BLD11NEW |  |  | PSZ-HEATCOOL:8_HEATC | 5.2193 | 6.0758 | 5.1446 | 6.4737 | 4.7205 | 5.3815 | 4.8958 | 7.016 | 5.8377 | 5.8386 | 8.1554 | 6.8578 | 8.8194 | 8.1355 | 8.8873 | 10.8037
BLD11NEW |  |  | PSZ-HEATCOOL:9_HEATC | 10.0667 | 11.1993 | 9.8423 | 10.8905 | 8.7259 | 9.2975 | 7.9923 | 11.1904 | 9.4629 | 9.2613 | 12.1069 | 10.2661 | 12.6088 | 11.3722 | 12.0343 | 12.8574
BLD11NEW |  |  | HVAC Efficiency
BLD11NEW | COP |  | Air Conditioning (COP) | 3.4616 | 3.4469 | 3.439 | 3.4641 | 3.4726 | 3.4566 | 3.4463 | 3.4654 | 3.4545 | 3.4619 | 3.4654 | 3.4563 | 3.4682 | 3.4556 | 3.4664 | 3.4564
BLD11NEW |  |  | GUESTROOM101 PTAC DXCOIL | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM102 PTAC DXCOIL | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM103 PTAC DXCOIL | 3.8 | 3.79 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM104 PTAC DXCOIL | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM105 PTAC DXCOIL | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM201 PTAC DXCOIL | 3.65 | 3.64 | 3.6 | 3.73 | 3.79 | 3.69 | 3.71 | 3.78 | 3.74 | 3.8 | 3.77 | 3.74 | 3.78 | 3.76 | 3.79 | 3.8
BLD11NEW |  |  | GUESTROOM202_205 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM206_208 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM209_212 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM213 PTAC DXCOIL | 3.77 | 3.74 | 3.72 | 3.79 | 3.8 | 3.78 | 3.72 | 3.8 | 3.79 | 3.8 | 3.8 | 3.79 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM214 PTAC DXCOIL | 3.78 | 3.79 | 3.77 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM215_218 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM219 PTAC DXCOIL | 3.71 | 3.72 | 3.69 | 3.72 | 3.78 | 3.7 | 3.78 | 3.73 | 3.67 | 3.77 | 3.73 | 3.67 | 3.74 | 3.7 | 3.74 | 3.78
BLD11NEW |  |  | GUESTROOM220_223 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM224 PTAC DXCOIL | 3.79 | 3.79 | 3.79 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM301 PTAC DXCOIL | 3.65 | 3.64 | 3.6 | 3.73 | 3.79 | 3.69 | 3.72 | 3.78 | 3.74 | 3.8 | 3.77 | 3.74 | 3.79 | 3.76 | 3.79 | 3.8
BLD11NEW |  |  | GUESTROOM302_305 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM306_308 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM309_312 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM313 PTAC DXCOIL | 3.76 | 3.73 | 3.7 | 3.77 | 3.8 | 3.76 | 3.71 | 3.79 | 3.77 | 3.8 | 3.78 | 3.77 | 3.8 | 3.78 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM314 PTAC DXCOIL | 3.77 | 3.78 | 3.75 | 3.8 | 3.8 | 3.78 | 3.8 | 3.8 | 3.79 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM315_318 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM319 PTAC DXCOIL | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM320_323 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM324 PTAC DXCOIL | 3.77 | 3.78 | 3.76 | 3.8 | 3.8 | 3.79 | 3.8 | 3.8 | 3.79 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
BLD11NEW |  |  | GUESTROOM401 PTAC DXCOIL | 3.51 | 3.48 | 3.42 | 3.59 | 3.68 | 3.54 | 3.64 | 3.65 | 3.61 | 3.71 | 3.65 | 3.63 | 3.68 | 3.66 | 3.7 | 3.8
BLD11NEW |  |  | GUESTROOM402_405 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM406_408 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM409_412 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM413 PTAC DXCOIL | 3.62 | 3.59 | 3.55 | 3.63 | 3.72 | 3.59 | 3.64 | 3.65 | 3.62 | 3.71 | 3.66 | 3.65 | 3.68 | 3.66 | 3.7 | 3.79
BLD11NEW |  |  | GUESTROOM414 PTAC DXCOIL | 3.62 | 3.61 | 3.56 | 3.66 | 3.77 | 3.61 | 3.8 | 3.68 | 3.65 | 3.77 | 3.68 | 3.68 | 3.71 | 3.71 | 3.75 | 3.8
BLD11NEW |  |  | GUESTROOM415_418 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM419 PTAC DXCOIL | 3.66 | 3.66 | 3.64 | 3.7 | 3.8 | 3.67 | 3.8 | 3.71 | 3.68 | 3.8 | 3.72 | 3.71 | 3.74 | 3.73 | 3.77 | 3.8
BLD11NEW |  |  | GUESTROOM420_423 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD11NEW |  |  | GUESTROOM424 PTAC DXCOIL | 3.62 | 3.62 | 3.58 | 3.66 | 3.77 | 3.62 | 3.8 | 3.68 | 3.64 | 3.77 | 3.69 | 3.68 | 3.71 | 3.7 | 3.74 | 3.8
BLD11NEW |  |  | PSZ-HEATCOOL:1_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW |  |  | PSZ-HEATCOOL:10_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW |  |  | PSZ-HEATCOOL:11_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW |  |  | PSZ-HEATCOOL:12_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW |  |  | PSZ-HEATCOOL:2_COOLC DXCOIL | 3.67 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW |  |  | PSZ-HEATCOOL:3_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW |  |  | PSZ-HEATCOOL:4_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW |  |  | PSZ-HEATCOOL:5_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW |  |  | PSZ-HEATCOOL:6_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW |  |  | PSZ-HEATCOOL:7_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
BLD11NEW |  |  | PSZ-HEATCOOL:8_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW |  |  | PSZ-HEATCOOL:9_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD11NEW | EffHeat |  | Heating Efficiency (%) | 0.83389 | 0.85278 | 0.84461 | 0.8545 | 0.83755 | 0.84827 | 0.84417 | 0.85785 | 0.85425 | 0.85168 | 0.86952 | 0.86689 | 0.88641 | 0.88801 | 0.88933 | 0.89476
BLD11NEW |  |  | FRONTSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | FRONTSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | FRONTSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | FRONTSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | FRONTSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | FRONTSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | FRONTSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | FRONTSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM101 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM102 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM103 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM104 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM105 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM201 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM202_205 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM206_208 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM209_212 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM213 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM214 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM215_218 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM219 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM220_223 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM224 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM301 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM302_305 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM306_308 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM309_312 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM313 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM314 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM315_318 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM319 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM320_323 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM324 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM401 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM402_405 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM406_408 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM409_412 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM413 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM414 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM415_418 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM419 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM420_423 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | GUESTROOM424 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | REARSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | REARSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | REARSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | REARSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | REARSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | REARSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | REARSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | REARSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD11NEW |  |  | PSZ-HEATCOOL:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:10_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:11_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:12_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | PSZ-HEATCOOL:9_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD11NEW |  |  | HVAC Control - Economizer
BLD11NEW |  |  | All GuestRoom & UnitHeater systems | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:10_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:11_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:12_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:3_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:4_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:6_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:7_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:8_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW |  |  | PSZ-HEATCOOL:9_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD11NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 14.25 | 14.72 | 15.61 | 14.51 | 13.11 | 14.96 | 14.25 | 13.84 | 15.51 | 13.42 | 14.07 | 15.42 | 14.15 | 15 | 14.18 | 12.94
BLD11NEW |  |  | FRONTSTAIRSFLR1 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.05
BLD11NEW |  |  | FRONTSTAIRSFLR2 UNIT HEATERFAN | 0 | 0.01 | 0.01 | 0.01 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
BLD11NEW |  |  | FRONTSTAIRSFLR3 UNIT HEATERFAN | 0 | 0.01 | 0.01 | 0.01 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
BLD11NEW |  |  | FRONTSTAIRSFLR4 UNIT HEATERFAN | 0.01 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.05 | 0.05 | 0.05 | 0.06 | 0.06 | 0.08
BLD11NEW |  |  | FRONTSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | FRONTSTORAGEFLR2 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | FRONTSTORAGEFLR3 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | FRONTSTORAGEFLR4 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
BLD11NEW |  |  | GUESTROOM101 PTACFAN | 0.09 | 0.1 | 0.1 | 0.09 | 0.09 | 0.09 | 0.11 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.08 | 0.07
BLD11NEW |  |  | GUESTROOM102 PTACFAN | 0.09 | 0.1 | 0.1 | 0.09 | 0.09 | 0.09 | 0.11 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.07
BLD11NEW |  |  | GUESTROOM103 PTACFAN | 0.1 | 0.11 | 0.11 | 0.1 | 0.09 | 0.1 | 0.11 | 0.09 | 0.1 | 0.09 | 0.09 | 0.1 | 0.1 | 0.09 | 0.09 | 0.08
BLD11NEW |  |  | GUESTROOM104 PTACFAN | 0.1 | 0.1 | 0.1 | 0.09 | 0.08 | 0.09 | 0.07 | 0.09 | 0.09 | 0.07 | 0.09 | 0.09 | 0.09 | 0.08 | 0.07 | 0.06
BLD11NEW |  |  | GUESTROOM105 PTACFAN | 0.1 | 0.1 | 0.1 | 0.1 | 0.09 | 0.09 | 0.07 | 0.09 | 0.1 | 0.08 | 0.09 | 0.1 | 0.09 | 0.09 | 0.08 | 0.07
BLD11NEW |  |  | GUESTROOM201 PTACFAN | 0.15 | 0.16 | 0.17 | 0.14 | 0.13 | 0.15 | 0.15 | 0.13 | 0.14 | 0.12 | 0.13 | 0.14 | 0.13 | 0.14 | 0.13 | 0.11
BLD11NEW |  |  | GUESTROOM202_205 PTACFAN | 0.42 | 0.43 | 0.47 | 0.43 | 0.41 | 0.46 | 0.54 | 0.41 | 0.47 | 0.45 | 0.42 | 0.47 | 0.43 | 0.46 | 0.45 | 0.43
BLD11NEW |  |  | GUESTROOM206_208 PTACFAN | 0.33 | 0.35 | 0.38 | 0.35 | 0.33 | 0.37 | 0.46 | 0.33 | 0.38 | 0.37 | 0.34 | 0.38 | 0.34 | 0.38 | 0.37 | 0.35
BLD11NEW |  |  | GUESTROOM209_212 PTACFAN | 0.4 | 0.42 | 0.46 | 0.42 | 0.4 | 0.44 | 0.53 | 0.4 | 0.46 | 0.43 | 0.41 | 0.46 | 0.41 | 0.45 | 0.43 | 0.42
BLD11NEW |  |  | GUESTROOM213 PTACFAN | 0.12 | 0.12 | 0.14 | 0.12 | 0.11 | 0.13 | 0.14 | 0.12 | 0.13 | 0.12 | 0.12 | 0.13 | 0.12 | 0.13 | 0.12 | 0.11
BLD11NEW |  |  | GUESTROOM214 PTACFAN | 0.12 | 0.12 | 0.13 | 0.12 | 0.1 | 0.12 | 0.1 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.11 | 0.11 | 0.1
BLD11NEW |  |  | GUESTROOM215_218 PTACFAN | 0.45 | 0.45 | 0.48 | 0.44 | 0.4 | 0.46 | 0.4 | 0.42 | 0.49 | 0.41 | 0.43 | 0.48 | 0.43 | 0.46 | 0.43 | 0.4
BLD11NEW |  |  | GUESTROOM219 PTACFAN | 0.14 | 0.14 | 0.15 | 0.14 | 0.13 | 0.15 | 0.13 | 0.14 | 0.16 | 0.13 | 0.14 | 0.16 | 0.14 | 0.15 | 0.14 | 0.13
BLD11NEW |  |  | GUESTROOM220_223 PTACFAN | 0.41 | 0.41 | 0.43 | 0.4 | 0.36 | 0.42 | 0.36 | 0.38 | 0.44 | 0.36 | 0.38 | 0.43 | 0.39 | 0.41 | 0.39 | 0.35
BLD11NEW |  |  | GUESTROOM224 PTACFAN | 0.12 | 0.12 | 0.13 | 0.11 | 0.1 | 0.12 | 0.1 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.11 | 0.11 | 0.1
BLD11NEW |  |  | GUESTROOM301 PTACFAN | 0.15 | 0.16 | 0.17 | 0.14 | 0.13 | 0.15 | 0.15 | 0.13 | 0.14 | 0.12 | 0.13 | 0.14 | 0.13 | 0.13 | 0.13 | 0.11
BLD11NEW |  |  | GUESTROOM302_305 PTACFAN | 0.42 | 0.43 | 0.48 | 0.43 | 0.41 | 0.46 | 0.55 | 0.41 | 0.47 | 0.45 | 0.42 | 0.48 | 0.43 | 0.47 | 0.45 | 0.44
BLD11NEW |  |  | GUESTROOM306_308 PTACFAN | 0.34 | 0.35 | 0.4 | 0.36 | 0.34 | 0.38 | 0.47 | 0.34 | 0.39 | 0.38 | 0.35 | 0.39 | 0.35 | 0.39 | 0.38 | 0.37
BLD11NEW |  |  | GUESTROOM309_312 PTACFAN | 0.41 | 0.43 | 0.48 | 0.43 | 0.41 | 0.46 | 0.55 | 0.41 | 0.47 | 0.45 | 0.42 | 0.48 | 0.43 | 0.46 | 0.45 | 0.44
BLD11NEW |  |  | GUESTROOM313 PTACFAN | 0.12 | 0.13 | 0.14 | 0.13 | 0.12 | 0.14 | 0.15 | 0.12 | 0.13 | 0.13 | 0.12 | 0.13 | 0.12 | 0.13 | 0.13 | 0.12
BLD11NEW |  |  | GUESTROOM314 PTACFAN | 0.12 | 0.12 | 0.14 | 0.12 | 0.1 | 0.13 | 0.1 | 0.11 | 0.13 | 0.1 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.1
BLD11NEW |  |  | GUESTROOM315_318 PTACFAN | 0.43 | 0.43 | 0.46 | 0.42 | 0.38 | 0.45 | 0.38 | 0.4 | 0.46 | 0.38 | 0.41 | 0.46 | 0.41 | 0.44 | 0.41 | 0.38
BLD11NEW |  |  | GUESTROOM319 PTACFAN | 0.11 | 0.12 | 0.12 | 0.11 | 0.1 | 0.12 | 0.1 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.12 | 0.11 | 0.1
BLD11NEW |  |  | GUESTROOM320_323 PTACFAN | 0.42 | 0.42 | 0.45 | 0.41 | 0.37 | 0.44 | 0.37 | 0.39 | 0.46 | 0.38 | 0.4 | 0.45 | 0.4 | 0.43 | 0.4 | 0.37
BLD11NEW |  |  | GUESTROOM324 PTACFAN | 0.12 | 0.12 | 0.13 | 0.12 | 0.1 | 0.13 | 0.1 | 0.11 | 0.13 | 0.11 | 0.11 | 0.12 | 0.11 | 0.12 | 0.11 | 0.1
BLD11NEW |  |  | GUESTROOM401 PTACFAN | 0.19 | 0.2 | 0.22 | 0.18 | 0.15 | 0.19 | 0.16 | 0.16 | 0.17 | 0.15 | 0.16 | 0.17 | 0.15 | 0.16 | 0.15 | 0.12
BLD11NEW |  |  | GUESTROOM402_405 PTACFAN | 0.54 | 0.57 | 0.63 | 0.57 | 0.51 | 0.61 | 0.61 | 0.54 | 0.6 | 0.52 | 0.54 | 0.58 | 0.54 | 0.57 | 0.54 | 0.46
BLD11NEW |  |  | GUESTROOM406_408 PTACFAN | 0.44 | 0.46 | 0.52 | 0.47 | 0.42 | 0.5 | 0.52 | 0.44 | 0.49 | 0.44 | 0.44 | 0.48 | 0.44 | 0.47 | 0.44 | 0.39
BLD11NEW |  |  | GUESTROOM409_412 PTACFAN | 0.54 | 0.57 | 0.63 | 0.57 | 0.51 | 0.61 | 0.61 | 0.54 | 0.6 | 0.52 | 0.54 | 0.58 | 0.54 | 0.57 | 0.54 | 0.46
BLD11NEW |  |  | GUESTROOM413 PTACFAN | 0.16 | 0.17 | 0.19 | 0.17 | 0.14 | 0.18 | 0.16 | 0.16 | 0.17 | 0.15 | 0.16 | 0.16 | 0.15 | 0.16 | 0.15 | 0.13
BLD11NEW |  |  | GUESTROOM414 PTACFAN | 0.16 | 0.16 | 0.18 | 0.16 | 0.13 | 0.17 | 0.12 | 0.15 | 0.16 | 0.13 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14 | 0.11
BLD11NEW |  |  | GUESTROOM415_418 PTACFAN | 0.55 | 0.57 | 0.62 | 0.56 | 0.48 | 0.59 | 0.45 | 0.53 | 0.59 | 0.48 | 0.52 | 0.57 | 0.51 | 0.54 | 0.5 | 0.41
BLD11NEW |  |  | GUESTROOM419 PTACFAN | 0.15 | 0.15 | 0.16 | 0.15 | 0.13 | 0.16 | 0.12 | 0.14 | 0.16 | 0.12 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.11
BLD11NEW |  |  | GUESTROOM420_423 PTACFAN | 0.55 | 0.56 | 0.61 | 0.55 | 0.47 | 0.59 | 0.44 | 0.52 | 0.59 | 0.47 | 0.52 | 0.56 | 0.51 | 0.54 | 0.5 | 0.41
BLD11NEW |  |  | GUESTROOM424 PTACFAN | 0.16 | 0.16 | 0.18 | 0.16 | 0.13 | 0.17 | 0.12 | 0.15 | 0.16 | 0.13 | 0.15 | 0.16 | 0.15 | 0.15 | 0.14 | 0.11
BLD11NEW |  |  | REARSTAIRSFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.02 | 0.01 | 0.02 | 0.03 | 0.03 | 0.04
BLD11NEW |  |  | REARSTAIRSFLR2 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.04
BLD11NEW |  |  | REARSTAIRSFLR3 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.04
BLD11NEW |  |  | REARSTAIRSFLR4 UNIT HEATERFAN | 0 | 0.02 | 0.01 | 0.02 | 0 | 0.01 | 0.01 | 0.03 | 0.02 | 0.02 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.07
BLD11NEW |  |  | REARSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02
BLD11NEW |  |  | REARSTORAGEFLR2 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02
BLD11NEW |  |  | REARSTORAGEFLR3 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02
BLD11NEW |  |  | REARSTORAGEFLR4 UNIT HEATERFAN | 0 | 0.02 | 0.01 | 0.02 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.01 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.05
BLD11NEW |  |  | PSZ-HEATCOOL:1_FAN | 0.51 | 0.52 | 0.5 | 0.51 | 0.45 | 0.46 | 0.4 | 0.49 | 0.53 | 0.44 | 0.49 | 0.52 | 0.49 | 0.5 | 0.46 | 0.37
BLD11NEW |  |  | PSZ-HEATCOOL:10_FAN | 0.24 | 0.25 | 0.27 | 0.24 | 0.21 | 0.25 | 0.23 | 0.23 | 0.26 | 0.22 | 0.23 | 0.25 | 0.23 | 0.24 | 0.23 | 0.2
BLD11NEW |  |  | PSZ-HEATCOOL:11_FAN | 0.22 | 0.23 | 0.25 | 0.22 | 0.19 | 0.23 | 0.21 | 0.21 | 0.23 | 0.2 | 0.21 | 0.23 | 0.21 | 0.22 | 0.21 | 0.19
BLD11NEW |  |  | PSZ-HEATCOOL:12_FAN | 0.36 | 0.38 | 0.43 | 0.37 | 0.3 | 0.39 | 0.28 | 0.35 | 0.37 | 0.3 | 0.34 | 0.34 | 0.33 | 0.33 | 0.32 | 0.27
BLD11NEW |  |  | PSZ-HEATCOOL:2_FAN | 0.76 | 0.78 | 0.81 | 0.75 | 0.72 | 0.75 | 0.84 | 0.72 | 0.8 | 0.75 | 0.73 | 0.8 | 0.74 | 0.78 | 0.75 | 0.68
BLD11NEW |  |  | PSZ-HEATCOOL:3_FAN | 0.08 | 0.08 | 0.08 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07 | 0.08 | 0.07 | 0.07 | 0.08 | 0.07 | 0.07 | 0.07 | 0.06
BLD11NEW |  |  | PSZ-HEATCOOL:4_FAN | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.45 | 0.43 | 0.43 | 0.45 | 0.43 | 0.43 | 0.43 | 0.43
BLD11NEW |  |  | PSZ-HEATCOOL:5_FAN | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.04
BLD11NEW |  |  | PSZ-HEATCOOL:6_FAN | 0.32 | 0.32 | 0.32 | 0.32 | 0.3 | 0.32 | 0.29 | 0.31 | 0.36 | 0.3 | 0.31 | 0.36 | 0.31 | 0.34 | 0.31 | 0.29
BLD11NEW |  |  | PSZ-HEATCOOL:7_FAN | 1.54 | 1.53 | 1.56 | 1.57 | 1.51 | 1.6 | 1.45 | 1.52 | 1.8 | 1.49 | 1.54 | 1.79 | 1.55 | 1.7 | 1.55 | 1.46
BLD11NEW |  |  | PSZ-HEATCOOL:8_FAN | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12 | 0.11 | 0.12 | 0.14 | 0.11 | 0.12 | 0.13 | 0.12 | 0.13 | 0.12 | 0.11
BLD11NEW |  |  | PSZ-HEATCOOL:9_FAN | 0.37 | 0.37 | 0.35 | 0.34 | 0.31 | 0.32 | 0.25 | 0.32 | 0.34 | 0.27 | 0.32 | 0.34 | 0.32 | 0.32 | 0.29 | 0.23
BLD11NEW |  | Utility Costs
BLD11NEW |  |  | Electric Utility Rates
BLD11NEW |  |  | Average Annual Rate ($/kWh) | 0.07845 | 0.10762 | 0.089033 | 0.10101 | 0.12307 | 0.094576 | 0.14496 | 0.068552 | 0.037255 | 0.071466 | 0.098348 | 0.037265 | 0.05456 | 0.071094 | 0.054757 | 0.091282
BLD11NEW |  |  | Total Cost ($/m2) | 14.22 | 18.02 | 15.05 | 15.58 | 17.95 | 14.83 | 19.98 | 10.16 | 5.46 | 9.59 | 14.32 | 5.3 | 8.11 | 9.98 | 7.94 | 14.14
BLD11NEW |  |  | Gas Utility Rates
BLD11NEW |  |  | Average Annual Rate ($/MJ) | 0.011459 | 0.0081727 | 0.0085306 | 0.010543 | 0.0084202 | 0.0080577 | 0.0084259 | 0.0099716 | 0.0071361 | 0.0083129 | 0.0087349 | 0.0071306 | 0.0079411 | 0.00857 | 0.0079388 | 0.0041676
BLD11NEW |  |  | Total Cost ($/m2) | 1.27 | 1.21 | 1.15 | 1.92 | 1.25 | 1.26 | 1.59 | 2.27 | 1.41 | 1.87 | 2.35 | 1.68 | 2.49 | 2.45 | 2.9 | 2.11
BLD11NEW |  |  | Total Utility Costs
BLD11NEW |  |  | Cost Intensity ($/m2) | 15.48 | 19.23 | 16.2 | 17.5 | 19.2 | 16.09 | 21.57 | 12.43 | 6.87 | 11.46 | 16.68 | 6.99 | 10.6 | 12.42 | 10.84 | 16.25
BLD11NEW |  | Energy - End Uses
BLD11NEW |  |  | Electricity (kWh)
BLD11NEW |  |  | Heating | 0 | 1894.4444 | 236.1111 | 2527.7778 | 0 | 169.4444 | 66.6667 | 6552.7778 | 1522.2222 | 1500 | 15277.7778 | 7819.4444 | 33308.3333 | 21052.7778 | 44769.4444 | 105275
BLD11NEW |  |  | Cooling | 226927.7778 | 172797.2222 | 178319.4444 | 122322.2222 | 94911.1111 | 132911.1111 | 65630.5556 | 98127.7778 | 89794.4444 | 51494.4444 | 80105.5556 | 68583.3333 | 73919.4444 | 51027.7778 | 49816.6667 | 34233.3333
BLD11NEW |  |  | Interior Lighting | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889
BLD11NEW |  |  | Exterior Lighting | 32950 | 32891.6667 | 32883.3333 | 32938.8889 | 32933.3333 | 32900 | 32863.8889 | 32897.2222 | 32891.6667 | 32844.4444 | 32852.7778 | 32858.3333 | 32880.5556 | 32838.8889 | 32830.5556 | 32633.3333
BLD11NEW |  |  | Interior Equipment | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667
BLD11NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Fans | 66786.1111 | 63622.2222 | 66594.4444 | 60619.4444 | 56950 | 62583.3333 | 54005.5556 | 56497.2222 | 63605.5556 | 52372.2222 | 55725 | 61272.2222 | 56063.8889 | 57608.3333 | 53847.2222 | 49119.4444
BLD11NEW |  |  | Pumps | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475
BLD11NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Total End Uses | 727294.4444 | 671838.8889 | 678666.6667 | 619038.8889 | 585422.2222 | 629194.4444 | 553197.2222 | 594705.5556 | 588444.4444 | 538841.6667 | 584588.8889 | 571163.8889 | 596800 | 563161.1111 | 581894.4444 | 621891.6667
BLD11NEW |  |  | Gas (MJ)
BLD11NEW |  |  | Heating | 7610 | 109320 | 82690 | 195030 | 71570 | 134910 | 189700 | 341720 | 227840 | 309960 | 475190 | 343500 | 623400 | 508190 | 783690 | 1289500
BLD11NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Equipment | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480
BLD11NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Water Systems | 247270 | 297050 | 268450 | 344990 | 335660 | 302930 | 376690 | 382640 | 375520 | 402260 | 415710 | 413990 | 444290 | 449470 | 491410 | 548430
BLD11NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Total End Uses | 444360 | 595850 | 540620 | 729500 | 596710 | 627320 | 755860 | 913840 | 792840 | 901700 | 1080380 | 946970 | 1257170 | 1147130 | 1464570 | 2027410
BLD11NEW |  |  | Purchased Cooling (MJ)
BLD11NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Purchased Heating (MJ)
BLD11NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Total Building (MJ) | 3062620 | 3014470 | 2983820 | 2958040 | 2704230 | 2892410 | 2747370 | 3054780 | 2911240 | 2841530 | 3184900 | 3003160 | 3405650 | 3174510 | 3559390 | 4266220
BLD11NEW |  | Energy - End Use Intensities
BLD11NEW |  |  | Electricity (MJ/m2)
BLD11NEW |  |  | Heating (elec) | 0 | 1.6992 | 0.21178 | 2.2673 | 0 | 0.15198 | 0.059797 | 5.8775 | 1.3654 | 1.3454 | 13.7034 | 7.0137 | 29.876 | 18.8833 | 40.1561 | 94.4267
BLD11NEW |  |  | Cooling (elec) | 203.5435 | 154.9909 | 159.9441 | 109.7172 | 85.1308 | 119.215 | 58.8675 | 88.016 | 80.5414 | 46.1881 | 71.8509 | 61.516 | 66.3022 | 45.7695 | 44.6832 | 30.7057
BLD11NEW |  |  | Interior Lighting (elec) | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531
BLD11NEW |  |  | Exterior Lighting (elec) | 29.5546 | 29.5023 | 29.4948 | 29.5446 | 29.5396 | 29.5097 | 29.4774 | 29.5072 | 29.5023 | 29.4599 | 29.4674 | 29.4724 | 29.4923 | 29.4549 | 29.4475 | 29.2706
BLD11NEW |  |  | Interior Equipment (elec) | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675
BLD11NEW |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Fans (elec) | 59.904 | 57.0661 | 59.7321 | 54.3728 | 51.0815 | 56.1343 | 48.4404 | 50.6753 | 57.0512 | 46.9754 | 49.9827 | 54.9583 | 50.2867 | 51.6719 | 48.2984 | 44.0578
BLD11NEW |  |  | Pumps (elec) | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605
BLD11NEW |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Total End Uses | 652.3486 | 602.6076 | 608.7318 | 555.2485 | 525.096 | 564.3576 | 496.1917 | 533.4227 | 527.8068 | 483.3154 | 524.3485 | 512.3069 | 535.3013 | 505.1288 | 521.9317 | 557.8073
BLD11NEW |  |  | Gas (MJ/m2)
BLD11NEW |  |  | Heating (gas) | 1.8961 | 27.2375 | 20.6025 | 48.5924 | 17.8319 | 33.6133 | 47.2644 | 85.1407 | 56.7671 | 77.2276 | 118.3953 | 85.5842 | 155.3223 | 126.6173 | 195.2591 | 321.2834
BLD11NEW |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Equipment (gas) | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096
BLD11NEW |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Water Systems (gas) | 61.6082 | 74.011 | 66.8853 | 85.9555 | 83.6309 | 75.4761 | 93.8536 | 95.3361 | 93.5621 | 100.2245 | 103.5756 | 103.1471 | 110.6964 | 111.987 | 122.4365 | 136.6433
BLD11NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Total End Uses | 110.7138 | 148.4581 | 134.6974 | 181.7575 | 148.6724 | 156.299 | 188.3252 | 227.6864 | 197.5389 | 224.6617 | 269.1805 | 235.9409 | 313.2283 | 285.8115 | 364.9027 | 505.1363
BLD11NEW |  |  | Purchased Cooling (MJ/m2)
BLD11NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Purchased Heating (MJ/m2)
BLD11NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Total Building (MJ/m2) | 763.0625 | 751.0658 | 743.4292 | 737.006 | 673.7684 | 720.6541 | 684.5169 | 761.1091 | 725.3456 | 707.9771 | 793.529 | 748.2478 | 848.5296 | 790.9403 | 886.8345 | 1062.9436
BLD11NEW |  | Peak Energy Demand
BLD11NEW |  |  | Electricity Peak Demand (kW)
BLD11NEW |  |  | Jan | 124.6128 | 117.7666 | 105.8863 | 103.6858 | 103.7877 | 98.7765 | 99.8788 | 106.1103 | 98.9278 | 95.66 | 115.4931 | 112.0504 | 127.9731 | 132.1267 | 131.4847 | 168.8783
BLD11NEW |  |  | Feb | 127.541 | 110.6627 | 106.5859 | 105.6214 | 107.326 | 102.1988 | 103.9422 | 99.2677 | 101.2073 | 98.3569 | 104.0381 | 99.9281 | 123.0143 | 118.3974 | 132.1283 | 162.8354
BLD11NEW |  |  | Mar | 127.0193 | 121.2078 | 122.1921 | 111.3101 | 103.7666 | 104.9989 | 101.3271 | 107.2209 | 103.0914 | 103.4942 | 102.1144 | 103.9978 | 101.3315 | 107.0084 | 112.0412 | 125.4281
BLD11NEW |  |  | Apr | 129.9654 | 129.2228 | 122.7207 | 118.4419 | 109.5378 | 119.9907 | 105.2864 | 108.8623 | 111.8068 | 104.1864 | 104.838 | 108.021 | 108.7511 | 102.5713 | 99.4344 | 101.6386
BLD11NEW |  |  | May | 135.9997 | 139.0163 | 140.1479 | 129.3534 | 112.492 | 126.1075 | 106.001 | 118.397 | 117.0363 | 107.9776 | 114.7314 | 115.4871 | 129.0578 | 107.6017 | 106.6902 | 100.9311
BLD11NEW |  |  | Jun | 142.8086 | 136.5865 | 157.9448 | 131.3073 | 110.0855 | 146.7476 | 107.4208 | 132.7664 | 122.9367 | 110.2953 | 124.8539 | 118.3702 | 128.1819 | 118.5598 | 120.2125 | 108.2105
BLD11NEW |  |  | Jul | 138.3714 | 142.4561 | 155.3112 | 139.7339 | 117.4158 | 144.7472 | 122.324 | 139.7121 | 129.334 | 115.7926 | 131.9037 | 124.479 | 133.3217 | 118.6099 | 126.5211 | 109.4506
BLD11NEW |  |  | Aug | 138.5665 | 147.2149 | 157.4236 | 132.5721 | 119.461 | 141.0174 | 107.2274 | 139.6047 | 128.2982 | 116.4081 | 136.5311 | 121.7585 | 133.2554 | 119.3863 | 126.6923 | 105.864
BLD11NEW |  |  | Sep | 136.4829 | 138.023 | 145.4244 | 126.5618 | 117.0194 | 130.5579 | 116.932 | 120.997 | 119.2162 | 120.3159 | 118.4515 | 116.1401 | 115.6864 | 116.5718 | 112.1642 | 99.8858
BLD11NEW |  |  | Oct | 135.9922 | 128.9657 | 125.6662 | 118.2343 | 109.7317 | 116.812 | 106.9797 | 116.3912 | 110.9709 | 104.4536 | 109.4076 | 109.3282 | 110.7377 | 104.4333 | 107.0584 | 110.9127
BLD11NEW |  |  | Nov | 126.6991 | 124.1325 | 109.6782 | 108.9818 | 106.4231 | 104.323 | 103.4185 | 111.5585 | 102.3679 | 102.2682 | 109.249 | 101.9172 | 100.5025 | 102.6255 | 114.3294 | 130.7895
BLD11NEW |  |  | Dec | 124.3119 | 124.4337 | 105.3982 | 107.2695 | 103.862 | 100.54 | 100.3676 | 101.135 | 97.9028 | 95.8909 | 110.9716 | 109.3385 | 129.5096 | 125.5131 | 130.2289 | 149.7648
BLD11NEW |  |  | Time of Peak Electrical Demand
BLD11NEW |  |  | Jan | 22-JAN-08:00 | 22-JAN-08:00 | 29-JAN-20:15 | 24-JAN-20:00 | 26-JAN-20:15 | 18-JAN-20:30 | 16-JAN-08:00 | 31-JAN-07:15 | 26-JAN-20:30 | 29-JAN-08:00 | 08-JAN-08:15 | 06-JAN-07:15 | 06-JAN-07:15 | 07-JAN-08:15 | 09-JAN-07:15 | 13-JAN-08:00
BLD11NEW |  |  | Feb | 25-FEB-08:00 | 20-FEB-20:30 | 28-FEB-20:15 | 20-FEB-20:30 | 12-FEB-08:00 | 27-FEB-20:15 | 15-FEB-20:15 | 01-FEB-07:15 | 14-FEB-20:30 | 21-FEB-20:30 | 11-FEB-08:15 | 12-FEB-20:00 | 04-FEB-08:15 | 26-FEB-08:15 | 02-FEB-07:15 | 04-FEB-08:15
BLD11NEW |  |  | Mar | 05-MAR-08:00 | 26-MAR-19:15 | 17-MAR-19:15 | 28-MAR-19:15 | 31-MAR-19:30 | 30-MAR-19:15 | 30-MAR-19:30 | 09-MAR-20:00 | 20-MAR-19:15 | 29-MAR-19:00 | 31-MAR-19:30 | 26-MAR-19:15 | 19-MAR-19:00 | 04-MAR-08:15 | 04-MAR-08:15 | 14-MAR-06:15
BLD11NEW |  |  | Apr | 01-APR-19:15 | 30-APR-19:15 | 02-APR-19:15 | 15-APR-19:15 | 11-APR-19:15 | 21-APR-19:15 | 29-APR-19:15 | 05-APR-19:15 | 22-APR-19:15 | 29-APR-19:15 | 29-APR-07:00 | 25-APR-19:30 | 02-APR-19:30 | 30-APR-19:30 | 15-APR-19:15 | 09-APR-07:15
BLD11NEW |  |  | May | 20-MAY-07:00 | 26-MAY-19:15 | 28-MAY-19:30 | 14-MAY-19:30 | 28-MAY-07:00 | 31-MAY-19:15 | 25-MAY-19:15 | 15-MAY-19:15 | 30-MAY-19:15 | 04-MAY-19:30 | 30-MAY-19:15 | 23-MAY-19:15 | 27-MAY-19:45 | 25-MAY-19:00 | 28-MAY-07:00 | 29-MAY-07:00
BLD11NEW |  |  | Jun | 27-JUN-19:15 | 13-JUN-19:30 | 27-JUN-19:45 | 19-JUN-19:00 | 28-JUN-19:15 | 27-JUN-19:15 | 17-JUN-07:00 | 30-JUN-19:45 | 28-JUN-19:30 | 18-JUN-07:00 | 16-JUN-19:30 | 27-JUN-19:30 | 29-JUN-19:00 | 25-JUN-20:30 | 14-JUN-19:00 | 24-JUN-07:00
BLD11NEW |  |  | Jul | 29-JUL-07:00 | 03-JUL-19:30 | 11-JUL-19:45 | 02-JUL-19:00 | 09-JUL-07:00 | 24-JUL-19:15 | 02-JUL-19:30 | 24-JUL-19:30 | 30-JUL-19:15 | 24-JUL-19:00 | 13-JUL-19:30 | 17-JUL-19:30 | 13-JUL-19:00 | 22-JUL-07:00 | 08-JUL-07:00 | 29-JUL-19:00
BLD11NEW |  |  | Aug | 21-AUG-19:15 | 06-AUG-19:15 | 01-AUG-19:30 | 14-AUG-19:30 | 13-AUG-07:00 | 04-AUG-19:15 | 27-AUG-19:15 | 17-AUG-19:15 | 01-AUG-19:15 | 06-AUG-19:45 | 04-AUG-19:15 | 29-AUG-19:15 | 25-AUG-19:15 | 11-AUG-19:45 | 13-AUG-19:30 | 13-AUG-07:00
BLD11NEW |  |  | Sep | 02-SEP-07:00 | 16-SEP-07:00 | 09-SEP-19:15 | 10-SEP-19:15 | 09-SEP-07:00 | 01-SEP-19:00 | 28-SEP-19:00 | 09-SEP-19:15 | 02-SEP-19:15 | 02-SEP-19:15 | 06-SEP-19:15 | 01-SEP-19:15 | 14-SEP-19:15 | 02-SEP-19:15 | 08-SEP-19:15 | 04-SEP-07:00
BLD11NEW |  |  | Oct | 07-OCT-07:00 | 29-OCT-19:15 | 02-OCT-19:15 | 21-OCT-19:15 | 07-OCT-07:00 | 03-OCT-19:15 | 16-OCT-19:15 | 20-OCT-19:15 | 01-OCT-19:15 | 09-OCT-19:15 | 31-OCT-19:15 | 01-OCT-19:15 | 08-OCT-19:15 | 06-OCT-19:15 | 07-OCT-19:15 | 22-OCT-07:15
BLD11NEW |  |  | Nov | 01-NOV-19:15 | 26-NOV-08:00 | 05-NOV-19:15 | 23-NOV-08:00 | 12-NOV-08:00 | 11-NOV-08:00 | 11-NOV-08:00 | 04-NOV-07:00 | 09-NOV-20:00 | 04-NOV-19:15 | 02-NOV-19:30 | 12-NOV-08:00 | 30-NOV-07:15 | 04-NOV-07:15 | 25-NOV-08:15 | 23-NOV-08:15
BLD11NEW |  |  | Dec | 16-DEC-08:00 | 03-DEC-08:00 | 13-DEC-20:30 | 31-DEC-08:00 | 18-DEC-20:15 | 09-DEC-08:00 | 17-DEC-08:00 | 21-DEC-07:15 | 08-DEC-20:30 | 31-DEC-20:00 | 31-DEC-08:15 | 12-DEC-07:15 | 31-DEC-08:15 | 11-DEC-07:15 | 31-DEC-08:15 | 29-DEC-08:00
BLD11NEW |  | Source Energy
BLD11NEW |  |  | Total Source Energy (GJ) | 9170.01 | 9435.08 | 8318.19 | 8293.41 | 7174.38 | 8787.28 | 6989.13 | 8653.9 | 7894.65 | 4363.84 | 8642.4 | 7856.52 | 8757.16 | 8299.83 | 8799.21 | 10210.97
BLD11NEW |  |  | Total Source Energy (MJ/m2) | 2284.74 | 2350.79 | 2072.51 | 2066.33 | 1787.52 | 2189.38 | 1741.37 | 2156.15 | 1966.98 | 1087.27 | 2153.29 | 1957.48 | 2181.88 | 2067.93 | 2192.35 | 2544.1
BLD11NEW |  | Water Consumption (m3)
BLD11NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Water Systems | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13
BLD11NEW |  |  | Total Building | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13
BLD11NEW |  | Emissions
BLD11NEW |  |  | Carbon Equivalent (kg) | 207473.4546 | 234843.6169 | 214621.4974 | 203841.3554 | 79176.1141 | 223523.5981 | 78280.1755 | 176963.2218 | 254675.8933 | 55506.1246 | 331155.4422 | 250395.4063 | 226950.7074 | 226485.7134 | 225588.5091 | 211552.2339
BLD11NEW |  |  | CO2 (kg) | 485012.4908 | 593371.9644 | 509964.9702 | 470788.9817 | 213747.2938 | 535308.427 | 211984.8261 | 407502.3659 | 601413.0037 | 140206.7292 | 775402.5223 | 592992.9794 | 536445.5337 | 538429.1841 | 535488.5941 | 543987.3185
BLD11NEW |  |  | NOX (kg) | 835.5595 | 767.3127 | 839.8893 | 870.2071 | 184.5391 | 853.9412 | 183.4628 | 762.793 | 1020.2289 | 192.444 | 1360.535 | 998.6569 | 918.8565 | 903.9327 | 907.2019 | 645.0769
BLD11NEW |  |  | SO2 (kg) | 3113.2332 | 3204.8255 | 2729.1972 | 2173.0203 | 1703.6656 | 3461.2379 | 1609.9424 | 2171.1532 | 2569.8364 | 416.7233 | 3939.9537 | 2494.4087 | 1408.8811 | 1504.0122 | 1373.7557 | 3166.2233
BLD11NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD11NEW |  |  | Hg (kg) | 0.0142 | 0.0091 | 0.0075 | 0.008 | 0.0008 | 0.0066 | 0.0008 | 0.0088 | 0.0101 | 0.0017 | 0.012 | 0.0098 | 0.0104 | 0.0105 | 0.0102 | 0.0109
BLD11NEW |  |  | Water for Electricity (m3) | 385.2904 | 1093.16 | 20159.4 | 3865.03 | 10278.7 | 17261.3 | 9712.92 | 135.0202 | 2672.01 | 5505.24 | 906.9553 | 2593.54 | 925.8999 | 35672.9 | 902.7739 | 635.3748

## Picture
DOE Commercial Building Benchmark - Small Hotel
First Floor
Upper Floors

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
| Sat |  |  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
| Sat |  |  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
| Sat |  |  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  |  |  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  |  |  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
[5 empty] | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
[5 empty] | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
[5 empty] | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
|  | ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
|  | ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
|  | GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 8.82 | 53.11 | 2769.31
[5 empty] | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 9.01
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
[5 empty] | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | 9.87 | 59.52 | 3103.54
[5 empty] | Sat, Sun, Hol | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | 10.17
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | INFIL_HALF_ON_SCH | Fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
|  | INFIL_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
SchGas |  | LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Other | [24 empty] | 24 | bar: 1 to 24
|  | LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
|  | LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
[5 empty] | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
|  | MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
[5 empty] | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
[5 empty] | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
[5 empty] | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
[5 empty] | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
| Sat |  |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Sun |  |  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
| Sat |  |  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
| Sun |  |  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  | HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | UnitHeater_ClgSP_Sch | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
|  | UnitHeater_HtgSP_Sch | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
SchGas | WD | GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
| Sat |  |  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
| Sun |  |  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
|  | LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
|  | Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
|  | Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | Laundry Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | Laundry Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
|  | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600