## 1
1 | Building Summary Small Office pre-1980 construction
UWG |  |  | Value | Value | Value
areaFloor |  | Total Floor Area (m2) | 511 | 511 | 511
nFloor |  | Number of Floors | 1 | 1 | 1
glazing |  | Total | 0.212 | 0.212 | 0.212
hCeiling |  | Floor to Ceiling Height (m) | 3.05 | 3.05 | 3.05
areaWall |  | Gross Dimensions - Total Area (m2) | 281.5 | 281.5 | 281.5
ver2hor |  | Wall to Skin Ratio | 0.36 | 0.32 | 0.32
areaRoof |  | Gross Dimensions - Total Area (m2) | 598.76 | 598.76 | 598.76
areaWindow |  | Total Area (m2) | 55.78 | 55.78 | 55.78

## 2
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD12PRE | Total | Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5003 | 59.6901 |  | 27.5104 | 19.4827 | 8.0729 | 0 | 11.3562 | 10 | 0.53819 | 275.1038 |  | 1.6833
BLD12PST | Total | Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5003 | 59.6901 |  | 27.5104 | 19.4827 | 10.76 | 0 | 11.3562 | 10 | 0.53819 | 275.1038 |  | 1.6833
BLD12NEW | Total | Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5003 | 59.6901 |  | 27.5104 | 10.7639 | 10.7639 | 0 | 11.3562 | 10 | 0.53819 | 275.1038 |  | 0.44889

## 3
3 |  | Location Summary
Building | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD12PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD12PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD12PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD12PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD12PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD12PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD12PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD12PRE | HVAC |  | Air Conditioning (kW) | 71.011 | 72.7273 | 72.6847 | 70.5526 | 58.1136 | 67.4994 | 51.8893 | 67.8842 | 63.0659 | 55.7092 | 72.5049 | 64.4113 | 76.9658 | 71.3413 | 75.8143 | 89.1574
BLD12PRE | HEAT |  | Heating (kW) | 90.7514 | 96.9206 | 97.7155 | 97.1176 | 84.6122 | 93.1624 | 77.9925 | 95.1553 | 80.3256 | 84.7093 | 98.1519 | 84.3606 | 106.0149 | 99.988 | 109.5438 | 142.87
BLD12PRE | COP |  | Air Conditioning (COP) | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.3847 | 3.39 | 3.3844 | 3.3873 | 3.3843 | 3.3844
BLD12PRE | EffHeat |  | Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD12PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 3.75 | 3.89 | 4.16 | 3.96 | 3.47 | 4.05 | 3.14 | 3.7 | 3.82 | 3.36 | 3.76 | 3.9 | 4.07 | 4.32 | 4.29 | 5.39
BLD12PST | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD12PST | RvalWall |  | R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
BLD12PST | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD12PST | RvalRoof |  | R-value attic floor (m2·K / W) | 2.38 | 2.6685 | 3.8287 | 2.4461 | 1.7612 | 3.6691 | 2.0013 | 3.0365 | 2.9851 | 2.7518 | 3.323 | 3.4533 | 3.9137 | 3.5943 | 4.403 | 5.6812
BLD12PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD12PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD12PST | HVAC |  | Air Conditioning (kW) | 50.4487 | 46.8436 | 44.7045 | 45.4655 | 42.19 | 39.4493 | 33.3792 | 41.6762 | 38.8313 | 35.224 | 43.2414 | 40.8817 | 42.4955 | 42.2795 | 41.6992 | 47.0188
BLD12PST | HEAT |  | Heating (kW) | 63.4042 | 64.318 | 61.8006 | 63.4195 | 62.4507 | 57.1514 | 52.2719 | 61.256 | 52.5935 | 56.6142 | 67.0157 | 57.4661 | 69.62 | 64.8935 | 69.7931 | 85.1086
BLD12PST | COP |  | PSZ-AC:1_COOLC DXCOIL | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
BLD12PST | EffHeat |  | PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12PST | Fan |  | Fan Max Flow Rate (m3/s ) | 2.56 | 2.47 | 2.53 | 2.46 | 2.52 | 2.37 | 2.01 | 2.22 | 2.34 | 2.13 | 2.39 | 2.47 | 2.44 | 2.55 | 2.47 | 2.84
BLD12NEW | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD12NEW | RvalWall |  | R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
BLD12NEW | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD12NEW | RvalRoof |  | R-value attic floor (m2·K / W) | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 6.5229 | 6.5229 | 6.5229 | 6.5229
BLD12NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD12NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD12NEW | HVAC |  | Air Conditioning (kW) | 38.6566 | 36.0325 | 37.2098 | 33.6 | 26.9743 | 28.349 | 26.5499 | 33.7549 | 29.9972 | 27.2727 | 32.9564 | 29.2012 | 32.0788 | 29.0537 | 29.3444 | 26.7576
BLD12NEW | HEAT |  | Heating (kW) | 50.4968 | 52.8923 | 51.3558 | 49.8258 | 41.8246 | 43.3609 | 42.6961 | 53.4567 | 42.4866 | 45.7119 | 55.3092 | 44.1257 | 55.7513 | 48.9374 | 53.808 | 57.3717
BLD12NEW | COP |  | PSZ-AC:1_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD12NEW | EffHeat |  | PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 2.02 | 1.98 | 2.07 | 1.84 | 1.62 | 1.72 | 1.61 | 1.87 | 1.81 | 1.65 | 1.86 | 1.77 | 1.81 | 1.77 | 1.75 | 1.62

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 78.95 | 4116.68
| Sat |  |  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
| Sun |  |  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 55.3 | 2883.5
| Sat |  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
| Sun |  |  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
SchOcc | WD |  |  |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1
| Sat |  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 597.6 | 3596.4 | 187526.57
| Sat |  |  |  | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 608.4
| Sun |  |  |  | Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 2743.2 | 143038.29
| Sat |  |  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 439.2
| Sun |  |  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
SchGas | WD |  | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.37 | 29.42 | 1534.04
| Sat |  |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.57
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.13
SchSWH | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
| Sat |  |  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
| Sun |  |  |  | Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04

## BuildingSummary
1 | Building Summary Small Office pre-1980 construction
UWG |  |  | Value | Value | Value
Program
|  | Building Name | Small Office Reference Building pre-1980 construction | Small Office Reference Building post-1980 construction | Small Office Reference Building new construction 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Office | Office | Office
Form
areaFloor |  | Total Floor Area (m2) | 511 | 511 | 511
|  | Building Shape | Rectangle | Rectangle | Rectangle
|  | Aspect Ratio | 1.5 | 1.5 | 1.5
nFloor |  | Number of Floors | 1 | 1 | 1
Window Fraction (Window to Wall Ratio)
|  | South | 0.244 | 0.244 | 0.244
|  | East | 0.198 | 0.198 | 0.198
|  | North | 0.198 | 0.198 | 0.198
|  | West | 0.198 | 0.198 | 0.198
glazing |  | Total | 0.212 | 0.212 | 0.212
Skylight/TDD Percentage
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | core zone with four perimeter zones | core zone with four perimeter zones | core zone with four perimeter zones
hCeiling |  | Floor to Ceiling Height (m) | 3.05 | 3.05 | 3.05
|  | Roof type | Built-up flat roof, insulation entirely above deck | Attic | Attic
Fabric
Exterior walls
|  | Construction Type | Steel-frame wall | Mass wall | Mass wall
areaWall |  | Gross Dimensions - Total Area (m2) | 281.5 | 281.5 | 281.5
|  | Net Dimensions - Total Area (m2) | 222 | 222 | 222
ver2hor |  | Wall to Skin Ratio | 0.36 | 0.32 | 0.32
Roof
|  | Construction Type | IEAD | Attic | Attic
areaRoof |  | Gross Dimensions - Total Area (m2) | 598.76 | 598.76 | 598.76
|  | Net Dimensions - Total Area (m2) | 598.76 | 598.76 | 598.76
|  | Roof to Skin Ratio | 0.64 | 0.68 | 0.68
Window Dimensions (m2)
|  | South | 16.73 | 16.73 | 16.73
|  | East | 11.16 | 11.16 | 11.16
|  | North | 16.73 | 16.73 | 16.73
|  | West | 11.16 | 11.16 | 11.16
areaWindow |  | Total Area (m2) | 55.78 | 55.78 | 55.78
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
|  | Foundation Type | Mass Floor | Mass Floor | Mass Floor
|  | Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
|  | Dimensions - Total Area (m2) | 511 | 511 | 511
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
|  | Dimensions - Total Area (m2) | 0 | 0 | 0
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 1022.46 | 1022.46 | 1022.46
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 1.68 | 1.68 | 0.45
HVAC
|  | System Type | PSZ-AC | PSZ-AC | PSZ-AC
|  | Heating Type | Gas furnace | Gas furnace | Gas furnace
|  | Cooling Type | Unitary DX | Unitary DX | Unitary DX
|  | Fan Control | Constant volume | Constant volume | Constant volume
Service Water Heating
|  | SWH Type | gas water heater | gas water heater | gas water heater
|  | Fuel | gas | gas | gas
|  | Thermal Efficiency (%) | 80 | 78 | 80
|  | Temperature Setpoint (ºC ) | 60 | 60 | 60
|  | Water Consumption (m3 ) | 17.63 | 17.63 | 17.63

## ZoneSummary
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
|  | Core_ZN | Yes | 1 | 149.66 | 456.46 | 3.05 | 0 | 0 | 18.5806 | 8.0546 | 19.4827 | 8.0729 |  | 11.3562 | 10 |  | 80.5463 |  | 0
|  | Perimeter_ZN_1 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 20.64 | 18.5806 | 6.1058 | 19.4827 | 8.0729 |  |  | 10 |  | 61.0582 |  | 2.3343
|  | Perimeter_ZN_2 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 19.4827 | 8.0729 |  |  | 10 |  | 36.2205 |  | 2.4577
|  | Perimeter_ZN_3 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 16.73 | 18.5806 | 6.1058 | 19.4827 | 8.0729 |  |  | 10 |  | 61.0582 |  | 2.3343
|  | Perimeter_ZN_4 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 19.4827 | 8.0729 |  |  | 10 |  | 36.2205 |  | 2.4577
BLD12PRE | Total | Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5003 | 59.6901 |  | 27.5104 | 19.4827 | 8.0729 | 0 | 11.3562 | 10 | 0.53819 | 275.1038 |  | 1.6833
|  | Core_ZN | Yes | 1 | 149.66 | 456.46 | 3.05 | 0 | 0 | 18.5806 | 8.0546 | 19.4827 | 10.76 |  | 11.3562 | 10 |  | 80.5463 |  | 0
|  | Perimeter_ZN_1 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 20.64 | 18.5806 | 6.1058 | 19.4827 | 10.76 |  |  | 10 |  | 61.0582 |  | 2.3343
|  | Perimeter_ZN_2 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 19.4827 | 10.76 |  |  | 10 |  | 36.2205 |  | 2.4577
|  | Perimeter_ZN_3 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 16.73 | 18.5806 | 6.1058 | 19.4827 | 10.76 |  |  | 10 |  | 61.0582 |  | 2.3343
|  | Perimeter_ZN_4 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 19.4827 | 10.76 |  |  | 10 |  | 36.2205 |  | 2.4577
|  | Attic | No | 1 | 567.98 | 720.19 | 1.268 | 0 | 0 | [8 empty] | 0 |  | 1
BLD12PST | Total | Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5003 | 59.6901 |  | 27.5104 | 19.4827 | 10.76 | 0 | 11.3562 | 10 | 0.53819 | 275.1038 |  | 1.6833
|  | Core_ZN | Yes | 1 | 149.66 | 456.46 | 3.05 | 0 | 0 | 18.5806 | 8.0546 | 10.7639 | 10.7639 |  | 11.3562 | 10 |  | 80.5463 |  | 0
|  | Perimeter_ZN_1 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 20.64 | 18.5806 | 6.1058 | 10.7639 | 10.7639 |  |  | 10 |  | 61.0582 |  | 0.62247
|  | Perimeter_ZN_2 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 10.7639 | 10.7639 |  |  | 10 |  | 36.2205 |  | 0.65537
|  | Perimeter_ZN_3 | Yes | 1 | 113.45 | 346.02 | 3.05 | 84.4501 | 16.73 | 18.5806 | 6.1058 | 10.7639 | 10.7639 |  |  | 10 |  | 61.0582 |  | 0.62247
|  | Perimeter_ZN_4 | Yes | 1 | 67.3 | 205.26 | 3.0499 | 56.3001 | 11.16 | 18.5806 | 3.6221 | 10.7639 | 10.7639 |  |  | 10 |  | 36.2205 |  | 0.65537
|  | Attic | No | 1 | 567.98 | 720.19 | 1.268 | 0 | 0 | [8 empty] | 0 |  | 1
BLD12NEW | Total | Total Conditioned Zones |  |  | 511.16 | 1559.02 |  | 281.5003 | 59.6901 |  | 27.5104 | 10.7639 | 10.7639 | 0 | 11.3562 | 10 | 0.53819 | 275.1038 |  | 0.44889

## LocationSummary
3 |  | Location Summary
Building | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD12PRE |  | Program
BLD12PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD12PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD12PRE
BLD12PRE |  | Fabric
BLD12PRE |  |  | Exterior walls
BLD12PRE | TypeWall |  | Construction Type | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall
BLD12PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD12PRE |  |  | Roof
BLD12PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD12PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD12PRE |  |  | Window
BLD12PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD12PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD12PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD12PRE |  |  | Skylights/TDD
BLD12PRE |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD12PRE |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD12PRE |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD12PRE |  |  | Foundation
BLD12PRE |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD12PRE |  |  | Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
BLD12PRE |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD12PRE |  | HVAC
BLD12PRE |  |  | HVAC Sizing
BLD12PRE | HVAC |  | Air Conditioning (kW) | 71.011 | 72.7273 | 72.6847 | 70.5526 | 58.1136 | 67.4994 | 51.8893 | 67.8842 | 63.0659 | 55.7092 | 72.5049 | 64.4113 | 76.9658 | 71.3413 | 75.8143 | 89.1574
BLD12PRE |  |  | PSZ-AC:1_COOLC DXCOIL | 14.0702 | 14.3172 | 13.3971 | 13.6299 | 10.8899 | 12.0158 | 8.7265 | 12.6538 | 11.8599 | 9.1845 | 11.4936 | 10.4201 | 10.1186 | 8.8957 | 8.4604 | 7.4131
BLD12PRE |  |  | PSZ-AC:2_COOLC DXCOIL | 15.3291 | 16.6759 | 17.3917 | 16.6398 | 14.9485 | 16.3623 | 16.8634 | 16.6356 | 14.2362 | 16.6376 | 19.157 | 16.3695 | 21.132 | 19.3499 | 21.0724 | 25.3241
BLD12PRE |  |  | PSZ-AC:3_COOLC DXCOIL | 11.784 | 11.6241 | 11.4591 | 11.2512 | 9.186 | 10.6232 | 7.1947 | 10.181 | 9.2621 | 7.9935 | 11.1126 | 10.185 | 12.225 | 12.0359 | 12.4006 | 15.7255
BLD12PRE |  |  | PSZ-AC:4_COOLC DXCOIL | 14.9502 | 14.8467 | 14.8018 | 14.1739 | 9.9629 | 12.8992 | 7.5833 | 14.8015 | 12.9973 | 10.091 | 19.5653 | 16.1566 | 21.7694 | 19.0392 | 21.779 | 24.9693
BLD12PRE |  |  | PSZ-AC:5_COOLC DXCOIL | 14.8775 | 15.2634 | 15.6351 | 14.8579 | 13.1264 | 15.5989 | 11.5214 | 13.6123 | 14.7104 | 11.8026 | 11.1763 | 11.2802 | 11.7208 | 12.0206 | 12.1019 | 15.7255
BLD12PRE | HEAT |  | Heating (kW) | 90.7514 | 96.9206 | 97.7155 | 97.1176 | 84.6122 | 93.1624 | 77.9925 | 95.1553 | 80.3256 | 84.7093 | 98.1519 | 84.3606 | 106.0149 | 99.988 | 109.5438 | 142.87
BLD12PRE |  |  | PSZ-AC:1_HEATC | 17.6629 | 18.9166 | 17.5832 | 18.9164 | 16.3392 | 16.9726 | 13.8495 | 17.9166 | 15.9559 | 15.0266 | 16.9817 | 15.0533 | 16.2834 | 14.7976 | 15.226 | 16.2227
BLD12PRE |  |  | PSZ-AC:2_HEATC | 18.6807 | 21.4194 | 23.1395 | 22.4704 | 21.752 | 22.5619 | 24.7384 | 22.8906 | 18.1037 | 24.6601 | 24.9315 | 21.0944 | 27.8436 | 26.4366 | 29.2766 | 39.2936
BLD12PRE |  |  | PSZ-AC:3_HEATC | 15.5936 | 15.8904 | 16.0384 | 15.883 | 13.3443 | 14.5616 | 10.7735 | 14.5899 | 11.674 | 12.0572 | 15.4432 | 13.0554 | 17.2255 | 16.3551 | 18.0996 | 24.2727
BLD12PRE |  |  | PSZ-AC:4_HEATC | 18.4589 | 19.2443 | 19.3211 | 18.7489 | 14.378 | 18.1143 | 11.8474 | 20.0032 | 16.6868 | 15.6869 | 24.6268 | 20.8513 | 27.4578 | 26.0619 | 28.8627 | 38.8082
BLD12PRE |  |  | PSZ-AC:5_HEATC | 20.3553 | 21.4499 | 21.6333 | 21.0989 | 18.7988 | 20.952 | 16.7837 | 19.755 | 17.9052 | 17.2784 | 16.1687 | 14.3062 | 17.2046 | 16.3367 | 18.079 | 24.2727
BLD12PRE |  |  | HVAC Efficiency
BLD12PRE | COP |  | Air Conditioning (COP) | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.3847 | 3.39 | 3.3844 | 3.3873 | 3.3843 | 3.3844
BLD12PRE |  |  | PSZ-AC:1_COOLC DXCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD12PRE |  |  | PSZ-AC:2_COOLC DXCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38 | 3.38 | 3.38
BLD12PRE |  |  | PSZ-AC:3_COOLC DXCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD12PRE |  |  | PSZ-AC:4_COOLC DXCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38
BLD12PRE |  |  | PSZ-AC:5_COOLC DXCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD12PRE | EffHeat |  | Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD12PRE |  |  | PSZ-AC:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD12PRE |  |  | PSZ-AC:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD12PRE |  |  | PSZ-AC:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD12PRE |  |  | PSZ-AC:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD12PRE |  |  | PSZ-AC:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD12PRE |  |  | HVAC Control - Economizer
BLD12PRE |  |  | PSZ-AC:1 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12PRE |  |  | PSZ-AC:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD12PRE |  |  | PSZ-AC:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12PRE |  |  | PSZ-AC:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12PRE |  |  | PSZ-AC:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 3.75 | 3.89 | 4.16 | 3.96 | 3.47 | 4.05 | 3.14 | 3.7 | 3.82 | 3.36 | 3.76 | 3.9 | 4.07 | 4.32 | 4.29 | 5.39
BLD12PRE |  |  | PSZ-AC:1_FAN | 0.71 | 0.73 | 0.72 | 0.73 | 0.65 | 0.7 | 0.53 | 0.65 | 0.72 | 0.55 | 0.58 | 0.63 | 0.53 | 0.54 | 0.49 | 0.45
BLD12PRE |  |  | PSZ-AC:2_FAN | 0.77 | 0.86 | 0.99 | 0.92 | 0.9 | 0.99 | 1.02 | 0.9 | 0.86 | 1.01 | 0.97 | 0.99 | 1.1 | 1.17 | 1.18 | 1.53
BLD12PRE |  |  | PSZ-AC:3_FAN | 0.65 | 0.65 | 0.69 | 0.66 | 0.55 | 0.64 | 0.43 | 0.58 | 0.56 | 0.48 | 0.61 | 0.62 | 0.68 | 0.73 | 0.73 | 0.95
BLD12PRE |  |  | PSZ-AC:4_FAN | 0.76 | 0.76 | 0.82 | 0.75 | 0.58 | 0.78 | 0.46 | 0.77 | 0.79 | 0.61 | 0.96 | 0.98 | 1.08 | 1.15 | 1.16 | 1.51
BLD12PRE |  |  | PSZ-AC:5_FAN | 0.86 | 0.89 | 0.94 | 0.9 | 0.79 | 0.94 | 0.7 | 0.8 | 0.89 | 0.71 | 0.64 | 0.68 | 0.68 | 0.73 | 0.73 | 0.95
BLD12PRE |  | Utility Costs
BLD12PRE |  |  | Electric Utility Rates
BLD12PRE |  |  | Average Annual Rate ($/kWh) | 0.082867 | 0.12251 | 0.1157 | 0.11481 | 0.13891 | 0.10093 | 0.15704 | 0.073127 | 0.074768 | 0.072814 | 0.058994 | 0.074805 | 0.074303 | 0.075839 | 0.074066 | 0.10004
BLD12PRE |  |  | Total Cost ($/m2) | 19.52 | 27.27 | 28.06 | 23.86 | 25.94 | 22.91 | 27.4 | 14.48 | 15.05 | 13.02 | 11.38 | 14.38 | 14.53 | 14.66 | 14.33 | 20.84
BLD12PRE |  |  | Gas Utility Rates
BLD12PRE |  |  | Average Annual Rate ($/MJ) | 0.011462 | 0.0080872 | 0.0082432 | 0.0096104 | 0.0085825 | 0.0076955 | 0.0085986 | 0.0096747 | 0.0068771 | 0.0084378 | 0.0082912 | 0.0068935 | 0.0078898 | 0.0080174 | 0.0078672 | 0.0041076
BLD12PRE |  |  | Total Cost ($/m2) | 0.26 | 0.79 | 0.59 | 1.79 | 0.44 | 0.94 | 1.08 | 3.2 | 1.66 | 2.22 | 3.57 | 2.27 | 4.52 | 3.66 | 5.74 | 5.31
BLD12PRE |  |  | Total Utility Costs
BLD12PRE |  |  | Cost Intensity ($/m2) | 19.78 | 28.06 | 28.65 | 25.65 | 26.38 | 23.86 | 28.48 | 17.68 | 16.7 | 15.24 | 14.96 | 16.65 | 19.05 | 18.31 | 20.07 | 26.16
BLD12PRE |  | Energy - End Uses
BLD12PRE |  |  | Electricity (kWh)
BLD12PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Cooling | 33680.5556 | 25519.4444 | 32494.4444 | 16638.8889 | 11297.2222 | 24986.1111 | 5625 | 11900 | 13191.6667 | 4300 | 8147.2222 | 7205.5556 | 7005.5556 | 4152.7778 | 3183.3333 | 2033.3333
BLD12PRE |  |  | Interior Lighting | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111
BLD12PRE |  |  | Exterior Lighting | 12088.8889 | 12086.1111 | 12083.3333 | 12080.5556 | 12072.2222 | 12069.4444 | 12075 | 12069.4444 | 12072.2222 | 12050 | 12069.4444 | 12063.8889 | 12063.8889 | 12061.1111 | 12052.7778 | 11977.7778
BLD12PRE |  |  | Interior Equipment | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444
BLD12PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Fans | 21769.4444 | 23300 | 26530.5556 | 24641.6667 | 19222.2222 | 26113.8889 | 18600 | 24336.1111 | 24725 | 22161.1111 | 25541.6667 | 26147.2222 | 28000 | 29694.4444 | 30802.7778 | 39602.7778
BLD12PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Total End Uses | 120416.6667 | 113783.3333 | 123986.1111 | 106241.6667 | 95466.6667 | 116047.2222 | 89180.5556 | 101183.3333 | 102866.6667 | 91388.8889 | 98638.8889 | 98294.4444 | 99944.4444 | 98786.1111 | 98919.4444 | 106494.4444
BLD12PRE |  |  | Gas (MJ)
BLD12PRE |  |  | Heating | 1380 | 39420 | 26170 | 83990 | 15170 | 52130 | 52880 | 157920 | 111960 | 123280 | 208820 | 156680 | 281120 | 221230 | 360610 | 648800
BLD12PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Water Systems | 10180 | 10580 | 10350 | 10970 | 10890 | 10630 | 11220 | 11270 | 11210 | 11420 | 11530 | 11520 | 11760 | 11800 | 12140 | 12590
BLD12PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Total End Uses | 11560 | 50000 | 36520 | 94950 | 26060 | 62760 | 64100 | 169190 | 123180 | 134710 | 220360 | 168200 | 292890 | 233030 | 372750 | 661390
BLD12PRE |  |  | Purchased Cooling (MJ)
BLD12PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Purchased Heating (MJ)
BLD12PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Total Building (MJ) | 445060 | 459620 | 482870 | 477420 | 369750 | 480530 | 385150 | 533440 | 493500 | 463700 | 575460 | 522060 | 652690 | 588660 | 728850 | 1044770
BLD12PRE |  | Energy - End Use Intensities
BLD12PRE |  |  | Electricity (MJ/m2)
BLD12PRE |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Cooling (elec) | 237.2056 | 179.7285 | 228.852 | 117.1844 | 79.5641 | 175.9723 | 39.6158 | 83.8094 | 92.9063 | 30.2841 | 57.3793 | 50.7473 | 49.3388 | 29.2472 | 22.4196 | 14.3204
BLD12PRE |  |  | Interior Lighting (elec) | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982
BLD12PRE |  |  | Exterior Lighting (elec) | 85.1397 | 85.1201 | 85.1006 | 85.081 | 85.0223 | 85.0027 | 85.0419 | 85.0027 | 85.0223 | 84.8658 | 85.0027 | 84.9636 | 84.9636 | 84.944 | 84.8854 | 84.3571
BLD12PRE |  |  | Interior Equipment (elec) | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292
BLD12PRE |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Fans (elec) | 153.3179 | 164.0973 | 186.8495 | 173.5464 | 135.3784 | 183.915 | 130.9962 | 171.3945 | 174.1333 | 156.0764 | 179.885 | 184.1498 | 197.1985 | 209.1322 | 216.9379 | 278.9146
BLD12PRE |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Total End Uses | 848.0711 | 801.3538 | 873.21 | 748.2393 | 672.3531 | 817.2979 | 628.0812 | 712.6144 | 724.4698 | 643.6341 | 694.6944 | 692.2686 | 703.8892 | 695.7313 | 696.6703 | 750.0196
BLD12PRE |  |  | Gas (MJ/m2)
BLD12PRE |  |  | Heating (gas) | 2.6997 | 77.1187 | 51.1973 | 164.3125 | 29.6776 | 101.9837 | 103.451 | 308.9444 | 219.0312 | 241.1769 | 408.5218 | 306.5185 | 549.9648 | 432.7999 | 705.4738 | 1269.2699
BLD12PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Water Systems (gas) | 19.9155 | 20.698 | 20.2481 | 21.461 | 21.3045 | 20.7958 | 21.9501 | 22.0479 | 21.9305 | 22.3413 | 22.5565 | 22.537 | 23.0065 | 23.0847 | 23.7499 | 24.6303
BLD12PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Total End Uses | 22.6152 | 97.8167 | 71.4453 | 185.754 | 50.9821 | 122.7796 | 125.401 | 330.9923 | 240.9813 | 263.5378 | 431.0979 | 329.0555 | 572.9908 | 455.8847 | 729.2237 | 1293.9001
BLD12PRE |  |  | Purchased Cooling (MJ/m2)
BLD12PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Purchased Heating (MJ/m2)
BLD12PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Total Building (MJ/m2) | 870.6863 | 899.1705 | 944.6553 | 933.9933 | 723.3547 | 940.0775 | 753.4823 | 1043.5871 | 965.4511 | 907.1524 | 1125.7923 | 1021.324 | 1276.88 | 1151.6159 | 1425.8745 | 2043.9197
BLD12PRE |  | Peak Energy Demand
BLD12PRE |  |  | Electricity Peak Demand (kW)
BLD12PRE |  |  | Jan | 28.6762 | 26.7046 | 25.8075 | 23.1631 | 25.063 | 23.5025 | 20.4259 | 21.1113 | 21.4371 | 20.5456 | 20.9967 | 21.447 | 21.348 | 21.5984 | 21.5685 | 22.6842
BLD12PRE |  |  | Feb | 29.6752 | 28.301 | 27.611 | 22.9225 | 24.2548 | 24.4696 | 22.8393 | 19.4759 | 23.626 | 19.6286 | 20.9967 | 20.3226 | 18.6302 | 19.7023 | 19.0125 | 22.6842
BLD12PRE |  |  | Mar | 30.3459 | 26.8307 | 31.605 | 26.3122 | 25.0004 | 25.8873 | 21.4816 | 23.9637 | 23.7985 | 22.0773 | 21.6324 | 23.1159 | 20.5973 | 21.7582 | 19.0773 | 22.6842
BLD12PRE |  |  | Apr | 31.5715 | 29.9317 | 32.0943 | 28.2874 | 26.5038 | 31.4788 | 24.0146 | 24.8344 | 26.7692 | 21.4025 | 22.5835 | 24.3204 | 22.3393 | 20.8544 | 20.945 | 20.9969
BLD12PRE |  |  | May | 33.7367 | 34.5277 | 35.7161 | 31.0812 | 25.42 | 34.1698 | 24.2849 | 27.6417 | 29.0745 | 24.6076 | 26.3403 | 26.2732 | 26.1294 | 24.2736 | 23.7187 | 23.7269
BLD12PRE |  |  | Jun | 34.629 | 34.9265 | 42.6415 | 33.6178 | 25.7042 | 40.6441 | 24.5461 | 33.5499 | 32.1672 | 25.5508 | 30.9039 | 28.7592 | 30.5353 | 29.0766 | 26.8905 | 26.2649
BLD12PRE |  |  | Jul | 33.7035 | 35.9481 | 41.6533 | 36.7158 | 27.2727 | 39.6101 | 26.6985 | 34.4766 | 33.3794 | 27.8574 | 31.9956 | 30.3833 | 30.1035 | 29.2567 | 29.0319 | 26.4039
BLD12PRE |  |  | Aug | 35.0524 | 35.8691 | 42.0369 | 34.0956 | 28.679 | 38.4254 | 25.4493 | 34.8846 | 33.0426 | 26.9649 | 31.0204 | 30.4068 | 30.2979 | 27.8518 | 27.7511 | 25.8292
BLD12PRE |  |  | Sep | 33.7155 | 34.0519 | 38.4711 | 32.0445 | 29.1573 | 37.377 | 29.8471 | 31.0816 | 29.0706 | 26.9709 | 27.8195 | 27.3815 | 26.9588 | 26.137 | 25.0234 | 21.9792
BLD12PRE |  |  | Oct | 32.9065 | 31.5147 | 32.4288 | 29.9283 | 27.0171 | 31.5794 | 24.3135 | 27.0256 | 26.5856 | 22.449 | 23.5639 | 25.8522 | 22.6241 | 23.3578 | 21.2609 | 22.6842
BLD12PRE |  |  | Nov | 30.7727 | 28.2988 | 29.7029 | 24.1569 | 25.5531 | 25.1025 | 21.8446 | 24.6058 | 22.9113 | 20.6754 | 23.162 | 22.6964 | 21.4754 | 21.9238 | 21.5685 | 22.6842
BLD12PRE |  |  | Dec | 28.847 | 27.2198 | 24.8315 | 22.621 | 25.3887 | 24.3896 | 21.2126 | 20.9108 | 22.2375 | 20.5456 | 20.9967 | 21.8707 | 21.348 | 21.5984 | 21.5685 | 22.6842
BLD12PRE |  |  | Time of Peak Electrical Demand
BLD12PRE |  |  | Jan | 24-JAN-13:00 | 03-JAN-13:00 | 26-JAN-15:39 | 23-JAN-15:00 | 26-JAN-13:00 | 30-JAN-16:00 | 27-JAN-15:09 | 05-JAN-16:00 | 25-JAN-15:20 | 02-JAN-16:30 | 02-JAN-16:30 | 12-JAN-16:00 | 02-JAN-16:40 | 02-JAN-08:09 | 02-JAN-16:30 | 02-JAN-08:09
BLD12PRE |  |  | Feb | 22-FEB-13:00 | 21-FEB-14:00 | 28-FEB-15:00 | 27-FEB-15:00 | 13-FEB-11:00 | 27-FEB-14:00 | 15-FEB-15:00 | 15-FEB-15:50 | 14-FEB-15:50 | 21-FEB-13:00 | 01-FEB-16:00 | 07-FEB-14:00 | 16-FEB-14:30 | 02-FEB-15:00 | 28-FEB-13:39 | 01-FEB-08:09
BLD12PRE |  |  | Mar | 27-MAR-14:00 | 27-MAR-15:20 | 17-MAR-15:20 | 28-MAR-15:50 | 31-MAR-14:09 | 31-MAR-14:39 | 20-MAR-14:00 | 09-MAR-15:00 | 02-MAR-15:09 | 29-MAR-15:30 | 31-MAR-15:30 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 22-MAR-14:39 | 01-MAR-08:09
BLD12PRE |  |  | Apr | 03-APR-14:30 | 17-APR-15:30 | 26-APR-15:30 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:39 | 18-APR-15:30 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:39 | 25-APR-15:00
BLD12PRE |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-15:39 | 15-MAY-14:00 | 30-MAY-13:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 15-MAY-15:20 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:39
BLD12PRE |  |  | Jun | 28-JUN-14:00 | 13-JUN-15:20 | 08-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 15-JUN-13:39 | 30-JUN-15:00 | 29-JUN-15:20 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
BLD12PRE |  |  | Jul | 13-JUL-14:00 | 31-JUL-14:30 | 11-JUL-15:00 | 03-JUL-15:30 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-13:30 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
BLD12PRE |  |  | Aug | 21-AUG-14:50 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-14:50 | 04-AUG-14:00 | 15-AUG-12:20 | 17-AUG-14:00 | 01-AUG-14:30 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:39 | 15-AUG-15:00
BLD12PRE |  |  | Sep | 11-SEP-14:00 | 15-SEP-14:00 | 11-SEP-15:30 | 11-SEP-13:50 | 25-SEP-12:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-14:00 | 01-SEP-15:30 | 05-SEP-14:00 | 06-SEP-14:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 07-SEP-15:00
BLD12PRE |  |  | Oct | 06-OCT-15:09 | 12-OCT-14:00 | 02-OCT-14:50 | 12-OCT-15:00 | 05-OCT-14:09 | 03-OCT-14:50 | 13-OCT-14:50 | 12-OCT-14:00 | 13-OCT-14:39 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-15:00 | 06-OCT-14:00 | 03-OCT-07:10
BLD12PRE |  |  | Nov | 07-NOV-14:00 | 01-NOV-14:00 | 13-NOV-14:00 | 22-NOV-14:00 | 20-NOV-13:39 | 10-NOV-16:40 | 14-NOV-16:00 | 03-NOV-13:00 | 08-NOV-14:00 | 14-NOV-16:40 | 02-NOV-14:50 | 10-NOV-16:49 | 06-NOV-16:00 | 21-NOV-16:49 | 06-NOV-16:49 | 01-NOV-07:10
BLD12PRE |  |  | Dec | 19-DEC-14:30 | 19-DEC-14:00 | 11-DEC-15:30 | 01-DEC-15:09 | 19-DEC-13:09 | 05-DEC-16:30 | 07-DEC-16:49 | 01-DEC-16:40 | 05-DEC-16:49 | 01-DEC-16:19 | 01-DEC-16:19 | 21-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-08:09
BLD12PRE |  | Source Energy
BLD12PRE |  |  | Total Source Energy (GJ) | 1450.55 | 1542.34 | 1451.68 | 1390.3 | 1092.16 | 1562.9 | 1063.64 | 1487.34 | 1363.23 | 720.21 | 1499.82 | 1357.78 | 1556.47 | 1490.64 | 1630.98 | 2091.67
BLD12PRE |  |  | Total Source Energy (MJ/m2) | 2837.78 | 3017.35 | 2839.98 | 2719.91 | 2136.65 | 3057.58 | 2080.85 | 2909.75 | 2666.95 | 1408.98 | 2934.16 | 2656.28 | 3045 | 2916.2 | 3190.75 | 4092.03
BLD12PRE |  | Water Consumption (m3)
BLD12PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Water Systems | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
BLD12PRE |  |  | Total Building | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
BLD12PRE |  | Emissions
BLD12PRE |  |  | Carbon Equivalent (kg) | 33232.9151 | 38855.2942 | 38086.6322 | 34438.1588 | 11626.9015 | 40271.7225 | 11577.9744 | 30355.6715 | 44241.9922 | 9085.2885 | 56562.969 | 43186.0206 | 39492.0903 | 40302.2344 | 40580.6826 | 41892.786
BLD12PRE |  |  | CO2 (kg) | 77072.1876 | 97841.5962 | 89922.2666 | 79221.7443 | 31144.9617 | 95973.3462 | 31164.7832 | 70046.5058 | 104329.9975 | 22829.8119 | 132818.445 | 102323.3871 | 94128.1569 | 96104.9221 | 97478.5236 | 109524.1091
BLD12PRE |  |  | NOX (kg) | 135.4095 | 127.5448 | 150.4946 | 147.9157 | 26.7238 | 154.9957 | 26.844 | 130.4299 | 177.6175 | 31.7767 | 231.3665 | 172.1109 | 157.7747 | 160.0666 | 160.0733 | 125.3267
BLD12PRE |  |  | SO2 (kg) | 515.4379 | 542.76 | 498.5782 | 372.9289 | 277.8069 | 638.3718 | 259.5217 | 369.4038 | 449.2309 | 70.6715 | 664.8077 | 429.2761 | 235.9654 | 263.8328 | 233.5631 | 542.2743
BLD12PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PRE |  |  | Hg (kg) | 0.0023 | 0.0015 | 0.0014 | 0.0014 | 0.0001 | 0.0012 | 0.0001 | 0.0015 | 0.0018 | 0.0003 | 0.002 | 0.0017 | 0.0018 | 0.0019 | 0.0017 | 0.0019
BLD12PRE |  |  | Water for Electricity (m3) | 63.7921 | 185.1389 | 3682.9 | 663.3218 | 1676.2 | 3183.65 | 1565.81 | 22.9723 | 467.0965 | 933.6897 | 153.0327 | 446.3341 | 155.0592 | 6257.51 | 153.4659 | 108.8028
BLD12PST |  | Program
BLD12PST |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD12PST |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD12PST
BLD12PST |  | Fabric
BLD12PST |  |  | Exterior walls
BLD12PST | TypeWall |  | Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
BLD12PST | RvalWall |  | R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
BLD12PST |  |  | Roof
BLD12PST | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD12PST | RvalRoof |  | R-value attic floor (m2·K / W) | 2.38 | 2.6685 | 3.8287 | 2.4461 | 1.7612 | 3.6691 | 2.0013 | 3.0365 | 2.9851 | 2.7518 | 3.323 | 3.4533 | 3.9137 | 3.5943 | 4.403 | 5.6812
BLD12PST |  |  | Window
BLD12PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD12PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD12PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD12PST |  |  | Skylights/TDD
BLD12PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD12PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD12PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD12PST |  |  | Foundation
BLD12PST |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD12PST |  |  | Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
BLD12PST |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD12PST |  | HVAC
BLD12PST |  |  | HVAC Sizing
BLD12PST | HVAC |  | Air Conditioning (kW) | 50.4487 | 46.8436 | 44.7045 | 45.4655 | 42.19 | 39.4493 | 33.3792 | 41.6762 | 38.8313 | 35.224 | 43.2414 | 40.8817 | 42.4955 | 42.2795 | 41.6992 | 47.0188
BLD12PST |  |  | PSZ-AC:1_COOLC DXCOIL | 11.6493 | 9.7612 | 9.5648 | 10.8164 | 9.7213 | 8.8665 | 7.3039 | 9.4818 | 9.0104 | 7.5198 | 9.4068 | 9.0939 | 9.479 | 8.7558 | 8.4679 | 7.4072
BLD12PST |  |  | PSZ-AC:2_COOLC DXCOIL | 10.7805 | 10.421 | 9.6413 | 9.8358 | 8.9899 | 8.2188 | 9.5843 | 9.0567 | 7.7723 | 9.1244 | 10.5268 | 9.2766 | 9.8009 | 10.1716 | 10.5625 | 12.1755
BLD12PST |  |  | PSZ-AC:3_COOLC DXCOIL | 7.6306 | 6.988 | 7.0058 | 6.7133 | 6.2694 | 6.2315 | 4.3408 | 6.3926 | 6.0449 | 5.4222 | 6.4919 | 5.9516 | 6.4165 | 6.5056 | 6.2392 | 7.8078
BLD12PST |  |  | PSZ-AC:4_COOLC DXCOIL | 11.0991 | 10.5669 | 9.724 | 9.7663 | 7.97 | 8.1324 | 5.3373 | 8.8729 | 7.6541 | 6.0938 | 8.9749 | 9.0571 | 9.4996 | 9.8776 | 9.4434 | 11.8204
BLD12PST |  |  | PSZ-AC:5_COOLC DXCOIL | 9.2893 | 9.1065 | 8.7687 | 8.3337 | 9.2395 | 8.0001 | 6.8129 | 7.8723 | 8.3495 | 7.0638 | 7.841 | 7.5025 | 7.2995 | 6.9689 | 6.9862 | 7.8078
BLD12PST | HEAT |  | Heating (kW) | 63.4042 | 64.318 | 61.8006 | 63.4195 | 62.4507 | 57.1514 | 52.2719 | 61.256 | 52.5935 | 56.6142 | 67.0157 | 57.4661 | 69.62 | 64.8935 | 69.7931 | 85.1086
BLD12PST |  |  | PSZ-AC:1_HEATC | 14.2953 | 14.7622 | 13.8887 | 15.2023 | 14.5055 | 13.4225 | 11.8744 | 15.4281 | 12.7 | 12.747 | 16.2539 | 13.5406 | 16.8726 | 14.6292 | 15.8054 | 16.2147
BLD12PST |  |  | PSZ-AC:2_HEATC | 13.1985 | 13.4275 | 12.6454 | 13.4296 | 13.398 | 11.6927 | 14.6234 | 12.627 | 10.7063 | 14.3557 | 14.7025 | 12.9868 | 15.8073 | 15.3533 | 16.3784 | 21.2705
BLD12PST |  |  | PSZ-AC:3_HEATC | 9.6372 | 9.5468 | 9.8191 | 9.2193 | 9.3058 | 8.9185 | 6.8076 | 9.4628 | 7.9908 | 8.5293 | 10.055 | 8.2162 | 10.2588 | 9.6768 | 10.3216 | 13.4193
BLD12PST |  |  | PSZ-AC:4_HEATC | 13.9066 | 14.0275 | 13.1813 | 13.6668 | 11.8249 | 11.9287 | 8.7258 | 12.3729 | 10.5712 | 10.204 | 14.3755 | 12.7363 | 15.4396 | 14.999 | 15.9797 | 20.7848
BLD12PST |  |  | PSZ-AC:5_HEATC | 12.3667 | 12.5541 | 12.2662 | 11.9015 | 13.4165 | 11.189 | 10.2407 | 11.3652 | 10.6251 | 10.7782 | 11.6288 | 9.9861 | 11.2418 | 10.2352 | 11.3082 | 13.4193
BLD12PST |  |  | HVAC Efficiency
BLD12PST |  |  | Air Conditioning (COP)
BLD12PST | COP |  | PSZ-AC:1_COOLC DXCOIL | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
BLD12PST |  |  | PSZ-AC:2_COOLC DXCOIL | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
BLD12PST |  |  | PSZ-AC:3_COOLC DXCOIL | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
BLD12PST |  |  | PSZ-AC:4_COOLC DXCOIL | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
BLD12PST |  |  | PSZ-AC:5_COOLC DXCOIL | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
BLD12PST |  |  | Heating Efficiency (%)
BLD12PST | EffHeat |  | PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12PST |  |  | PSZ-AC:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12PST |  |  | PSZ-AC:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12PST |  |  | PSZ-AC:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12PST |  |  | PSZ-AC:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12PST |  |  | HVAC Control - Economizer
BLD12PST |  |  | PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12PST |  |  | PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12PST |  |  | PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12PST |  |  | PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12PST |  |  | PSZ-AC:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12PST | Fan |  | Fan Max Flow Rate (m3/s ) | 2.56 | 2.47 | 2.53 | 2.46 | 2.52 | 2.37 | 2.01 | 2.22 | 2.34 | 2.13 | 2.39 | 2.47 | 2.44 | 2.55 | 2.47 | 2.84
BLD12PST |  |  | PSZ-AC:1_FAN | 0.57 | 0.55 | 0.55 | 0.57 | 0.57 | 0.54 | 0.44 | 0.54 | 0.54 | 0.45 | 0.55 | 0.55 | 0.56 | 0.53 | 0.51 | 0.45
BLD12PST |  |  | PSZ-AC:2_FAN | 0.53 | 0.51 | 0.51 | 0.52 | 0.54 | 0.48 | 0.58 | 0.45 | 0.47 | 0.55 | 0.52 | 0.56 | 0.56 | 0.61 | 0.59 | 0.74
BLD12PST |  |  | PSZ-AC:3_FAN | 0.39 | 0.37 | 0.41 | 0.36 | 0.38 | 0.38 | 0.26 | 0.35 | 0.37 | 0.33 | 0.37 | 0.36 | 0.37 | 0.39 | 0.38 | 0.47
BLD12PST |  |  | PSZ-AC:4_FAN | 0.56 | 0.54 | 0.54 | 0.53 | 0.47 | 0.49 | 0.32 | 0.44 | 0.46 | 0.37 | 0.51 | 0.55 | 0.54 | 0.6 | 0.57 | 0.71
BLD12PST |  |  | PSZ-AC:5_FAN | 0.51 | 0.5 | 0.52 | 0.48 | 0.56 | 0.48 | 0.41 | 0.44 | 0.5 | 0.43 | 0.44 | 0.45 | 0.41 | 0.42 | 0.42 | 0.47
BLD12PST |  | Utility Costs
BLD12PST |  |  | Electric Utility Rates
BLD12PST |  |  | Average Annual Rate ($/kWh) | 0.080979 | 0.12147 | 0.11688 | 0.11575 | 0.13943 | 0.1007 | 0.15794 | 0.073734 | 0.074912 | 0.07292 | 0.060417 | 0.074939 | 0.074532 | 0.076545 | 0.074348 | 0.099185
BLD12PST |  |  | Total Cost ($/m2) | 17.37 | 23.56 | 24.03 | 20.56 | 23.85 | 18.91 | 24.32 | 12.46 | 12.78 | 11.38 | 10.18 | 12.46 | 12.53 | 12.63 | 12.17 | 16.79
BLD12PST |  |  | Gas Utility Rates
BLD12PST |  |  | Average Annual Rate ($/MJ) | 0.011463 | 0.0081042 | 0.0083835 | 0.009707 | 0.0085533 | 0.0077908 | 0.0086393 | 0.0097157 | 0.0069116 | 0.0084318 | 0.0083085 | 0.006901 | 0.0079201 | 0.0080248 | 0.0078873 | 0.0041031
BLD12PST |  |  | Total Cost ($/m2) | 0.24 | 0.49 | 0.34 | 1.02 | 0.28 | 0.46 | 0.65 | 1.45 | 0.75 | 1.03 | 1.77 | 1.06 | 2.22 | 1.79 | 2.69 | 2.57
BLD12PST |  |  | Total Utility Costs
BLD12PST |  |  | Cost Intensity ($/m2) | 17.61 | 24.05 | 24.37 | 21.58 | 24.14 | 19.37 | 24.98 | 13.91 | 13.53 | 12.41 | 11.95 | 13.52 | 14.75 | 14.42 | 14.86 | 19.36
BLD12PST |  | Energy - End Uses
BLD12PST |  |  | Electricity (kWh)
BLD12PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Cooling | 29050 | 19688.8889 | 24063.8889 | 11577.7778 | 8830.5556 | 16677.7778 | 2800 | 8219.4444 | 8447.2222 | 2588.8889 | 6444.4444 | 5191.6667 | 5513.8889 | 3505.5556 | 2608.3333 | 1900
BLD12PST |  |  | Interior Lighting | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111 | 28511.1111
BLD12PST |  |  | Exterior Lighting | 12088.8889 | 12086.1111 | 12083.3333 | 12080.5556 | 12072.2222 | 12069.4444 | 12075 | 12069.4444 | 12072.2222 | 12050 | 12069.4444 | 12063.8889 | 12063.8889 | 12061.1111 | 12052.7778 | 11977.7778
BLD12PST |  |  | Interior Equipment | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444
BLD12PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Fans | 15622.2222 | 14497.2222 | 16083.3333 | 14233.3333 | 13658.3333 | 14363.8889 | 10969.4444 | 13205.5556 | 13822.2222 | 12288.8889 | 14761.1111 | 14844.4444 | 15461.1111 | 15888.8889 | 16155.5556 | 19766.6667
BLD12PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Total End Uses | 109641.6667 | 99150 | 105108.3333 | 90772.2222 | 87438.8889 | 95988.8889 | 78722.2222 | 86372.2222 | 87222.2222 | 79805.5556 | 86155.5556 | 84975 | 85913.8889 | 84330.5556 | 83694.4444 | 86522.2222
BLD12PST |  |  | Gas (MJ)
BLD12PST |  |  | Heating | 330 | 19780 | 10070 | 42730 | 5830 | 19610 | 27060 | 64750 | 43820 | 50690 | 97170 | 66610 | 131430 | 102110 | 161660 | 307150
BLD12PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Water Systems | 10430 | 10840 | 10600 | 11230 | 11160 | 10880 | 11490 | 11540 | 11480 | 11700 | 11810 | 11800 | 12050 | 12090 | 12430 | 12900
BLD12PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Total End Uses | 10760 | 30620 | 20680 | 53960 | 16990 | 30490 | 38560 | 76290 | 55300 | 62390 | 108980 | 78410 | 143480 | 114200 | 174100 | 320050
BLD12PST |  |  | Purchased Cooling (MJ)
BLD12PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Purchased Heating (MJ)
BLD12PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Total Building (MJ) | 405460 | 387560 | 399060 | 380740 | 331770 | 376050 | 321960 | 387230 | 369300 | 349690 | 419140 | 384320 | 452770 | 417790 | 475400 | 631540
BLD12PST |  | Energy - End Use Intensities
BLD12PST |  |  | Electricity (MJ/m2)
BLD12PST |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Cooling (elec) | 204.5935 | 138.665 | 169.4773 | 81.54 | 62.1919 | 117.4583 | 19.7199 | 57.8879 | 59.4921 | 18.233 | 45.387 | 36.5639 | 38.8332 | 24.6889 | 18.37 | 13.3813
BLD12PST |  |  | Interior Lighting (elec) | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982 | 200.7982
BLD12PST |  |  | Exterior Lighting (elec) | 85.1397 | 85.1201 | 85.1006 | 85.081 | 85.0223 | 85.0027 | 85.0419 | 85.0027 | 85.0223 | 84.8658 | 85.0027 | 84.9636 | 84.9636 | 84.944 | 84.8854 | 84.3571
BLD12PST |  |  | Interior Equipment (elec) | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292
BLD12PST |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Fans (elec) | 110.0243 | 102.1011 | 113.2718 | 100.2426 | 96.193 | 101.1621 | 77.2557 | 93.0041 | 97.3472 | 86.5482 | 103.9596 | 104.5465 | 108.8896 | 111.9023 | 113.7804 | 139.2128
BLD12PST |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Total End Uses | 772.1848 | 698.2941 | 740.2575 | 639.291 | 615.815 | 676.031 | 554.4252 | 608.3027 | 614.2891 | 562.0549 | 606.7767 | 598.4623 | 605.0747 | 593.9236 | 589.4436 | 609.3591
BLD12PST |  |  | Gas (MJ/m2)
BLD12PST |  |  | Heating (gas) | 0.64559 | 38.6963 | 19.7003 | 83.5942 | 11.4054 | 38.3637 | 52.9384 | 126.6727 | 85.7266 | 99.1666 | 190.097 | 130.3114 | 257.1211 | 199.7613 | 316.2611 | 600.8882
BLD12PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Water Systems (gas) | 20.4046 | 21.2067 | 20.7371 | 21.9696 | 21.8327 | 21.2849 | 22.4783 | 22.5761 | 22.4587 | 22.8891 | 23.1043 | 23.0847 | 23.5738 | 23.6521 | 24.3172 | 25.2367
BLD12PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Total End Uses | 21.0502 | 59.903 | 40.457 | 105.5638 | 33.2381 | 59.6486 | 75.4363 | 149.2488 | 108.1853 | 122.0557 | 213.2013 | 153.3962 | 280.6949 | 223.4134 | 340.5979 | 626.1249
BLD12PST |  |  | Purchased Cooling (MJ/m2)
BLD12PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Purchased Heating (MJ/m2)
BLD12PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Total Building (MJ/m2) | 793.2154 | 758.197 | 780.6949 | 744.8548 | 649.0531 | 735.6796 | 629.8615 | 757.5515 | 722.4744 | 684.1107 | 819.9781 | 751.8585 | 885.7696 | 817.337 | 930.0415 | 1235.5036
BLD12PST |  | Peak Energy Demand
BLD12PST |  |  | Electricity Peak Demand (kW)
BLD12PST |  |  | Jan | 25.0503 | 22.3294 | 20.2709 | 18.8364 | 21.9445 | 20.2225 | 19.0165 | 19.246 | 17.8711 | 19.1458 | 19.4348 | 19.5422 | 19.5062 | 19.6402 | 19.5423 | 19.9422
BLD12PST |  |  | Feb | 25.8379 | 22.8088 | 21.4702 | 18.4885 | 21.3327 | 19.0165 | 19.4719 | 16.8101 | 19.1827 | 17.1785 | 19.4348 | 17.5392 | 16.7548 | 17.6515 | 16.9039 | 19.9422
BLD12PST |  |  | Mar | 26.3823 | 22.5334 | 24.7281 | 20.6859 | 22.1632 | 20.3776 | 17.8252 | 19.5217 | 19.3964 | 18.9571 | 18.7719 | 19.6249 | 17.8994 | 19.1912 | 16.9763 | 19.9422
BLD12PST |  |  | Apr | 27.2797 | 24.7805 | 25.1052 | 23.2048 | 23.4189 | 24.3487 | 20.1312 | 20.4504 | 21.8661 | 18.3781 | 19.2447 | 20.6809 | 19.0766 | 18.717 | 18.127 | 18.2628
BLD12PST |  |  | May | 29.046 | 28.7199 | 29.0296 | 25.8534 | 23.2819 | 27.0334 | 20.2368 | 22.8473 | 23.9504 | 20.517 | 22.8007 | 22.4564 | 22.5619 | 20.5546 | 20.4155 | 20.5938
BLD12PST |  |  | Jun | 30.4578 | 29.2675 | 34.0954 | 28.0631 | 23.5396 | 31.5467 | 21.4939 | 27.5848 | 26.309 | 21.546 | 26.2318 | 24.3068 | 25.9778 | 24.4589 | 23.0876 | 22.5513
BLD12PST |  |  | Jul | 29.6852 | 30.3038 | 33.5502 | 30.5402 | 24.9678 | 31.0481 | 23.0377 | 28.2 | 27.2576 | 23.2712 | 27.2634 | 25.7908 | 25.9676 | 24.94 | 24.7471 | 22.715
BLD12PST |  |  | Aug | 30.0979 | 30.0656 | 33.5296 | 27.7247 | 26.0455 | 30.2566 | 20.9995 | 28.2202 | 26.9035 | 22.7035 | 26.7519 | 25.6349 | 25.7775 | 24.0286 | 23.738 | 22.4282
BLD12PST |  |  | Sep | 29.0553 | 28.3019 | 30.5567 | 26.1343 | 26.3297 | 29.2697 | 25.1179 | 24.8661 | 23.6522 | 22.5853 | 23.8649 | 23.0505 | 23.1985 | 22.1037 | 21.7479 | 19.096
BLD12PST |  |  | Oct | 28.4959 | 26.7123 | 25.8688 | 24.0483 | 24.1082 | 24.7541 | 20.856 | 22.2185 | 21.6596 | 19.163 | 20.9863 | 21.7305 | 19.5021 | 20.0656 | 18.7002 | 19.9422
BLD12PST |  |  | Nov | 26.5808 | 23.6423 | 23.4032 | 19.95 | 23.3961 | 21.9406 | 20.294 | 20.5892 | 20.0228 | 19.258 | 20.478 | 20.2019 | 19.5398 | 19.9756 | 19.5423 | 19.9422
BLD12PST |  |  | Dec | 24.8233 | 22.3849 | 19.8759 | 17.9743 | 22.7093 | 20.8355 | 19.4981 | 19.246 | 19.851 | 19.1458 | 19.4608 | 19.7989 | 19.5062 | 19.6402 | 19.5423 | 19.9422
BLD12PST |  |  | Time of Peak Electrical Demand
BLD12PST |  |  | Jan | 23-JAN-15:00 | 03-JAN-13:00 | 27-JAN-14:00 | 23-JAN-16:00 | 26-JAN-13:00 | 18-JAN-16:49 | 02-JAN-16:00 | 02-JAN-16:49 | 26-JAN-15:00 | 02-JAN-16:30 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-08:09 | 02-JAN-16:30 | 02-JAN-08:09
BLD12PST |  |  | Feb | 22-FEB-15:00 | 23-FEB-15:39 | 28-FEB-16:40 | 27-FEB-16:00 | 13-FEB-14:00 | 27-FEB-15:00 | 15-FEB-15:00 | 15-FEB-15:00 | 14-FEB-15:00 | 22-FEB-14:00 | 01-FEB-16:00 | 07-FEB-14:00 | 22-FEB-13:20 | 02-FEB-15:00 | 28-FEB-13:39 | 01-FEB-08:09
BLD12PST |  |  | Mar | 13-MAR-15:00 | 28-MAR-14:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:00 | 31-MAR-15:00 | 01-MAR-14:39 | 09-MAR-15:00 | 02-MAR-15:00 | 29-MAR-15:50 | 31-MAR-14:00 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 22-MAR-14:09 | 01-MAR-08:09
BLD12PST |  |  | Apr | 03-APR-15:00 | 21-APR-15:30 | 26-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:50 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:00 | 18-APR-15:00 | 28-APR-15:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:30 | 25-APR-15:00
BLD12PST |  |  | May | 24-MAY-14:00 | 18-MAY-15:39 | 30-MAY-15:00 | 15-MAY-15:09 | 30-MAY-15:50 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
BLD12PST |  |  | Jun | 28-JUN-14:00 | 13-JUN-15:00 | 28-JUN-15:00 | 19-JUN-15:00 | 30-JUN-15:30 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-15:30 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 30-JUN-14:00 | 14-JUN-15:00 | 21-JUN-15:00
BLD12PST |  |  | Jul | 13-JUL-15:39 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-15:50 | 31-JUL-15:00 | 24-JUL-14:00 | 03-JUL-15:30 | 17-JUL-15:39 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
BLD12PST |  |  | Aug | 21-AUG-15:00 | 31-AUG-15:00 | 01-AUG-15:00 | 17-AUG-15:39 | 08-AUG-15:09 | 04-AUG-15:00 | 15-AUG-12:00 | 17-AUG-15:00 | 01-AUG-15:30 | 07-AUG-15:20 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-14:30
BLD12PST |  |  | Sep | 11-SEP-14:00 | 15-SEP-14:00 | 11-SEP-15:00 | 11-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-15:30 | 08-SEP-15:00 | 21-SEP-15:00 | 01-SEP-15:00 | 27-SEP-15:00 | 06-SEP-15:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 07-SEP-15:00
BLD12PST |  |  | Oct | 06-OCT-15:00 | 06-OCT-15:00 | 02-OCT-15:00 | 12-OCT-15:00 | 05-OCT-14:30 | 03-OCT-15:30 | 13-OCT-15:00 | 12-OCT-15:00 | 11-OCT-15:00 | 17-OCT-15:30 | 31-OCT-13:30 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-15:00 | 06-OCT-14:00 | 03-OCT-07:10
BLD12PST |  |  | Nov | 07-NOV-14:00 | 03-NOV-14:39 | 13-NOV-16:30 | 22-NOV-15:30 | 09-NOV-16:00 | 10-NOV-16:40 | 14-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 14-NOV-16:00 | 02-NOV-14:39 | 10-NOV-16:49 | 06-NOV-16:00 | 21-NOV-16:49 | 06-NOV-16:49 | 01-NOV-07:10
BLD12PST |  |  | Dec | 15-DEC-15:39 | 19-DEC-15:30 | 11-DEC-15:00 | 13-DEC-15:00 | 18-DEC-16:49 | 05-DEC-16:30 | 07-DEC-16:49 | 01-DEC-16:40 | 08-DEC-16:49 | 01-DEC-16:19 | 12-DEC-16:00 | 21-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-08:09
BLD12PST |  | Source Energy
BLD12PST |  |  | Total Source Energy (GJ) | 1320.99 | 1329.85 | 1219.41 | 1158.21 | 992.8 | 1269.37 | 919.24 | 1195.22 | 1102.23 | 568.61 | 1218.84 | 1100.65 | 1219.73 | 1180 | 1225.69 | 1462.11
BLD12PST |  |  | Total Source Energy (MJ/m2) | 2584.3 | 2601.65 | 2385.59 | 2265.86 | 1942.26 | 2483.33 | 1798.35 | 2338.26 | 2156.34 | 1112.4 | 2384.48 | 2153.24 | 2386.21 | 2308.48 | 2397.86 | 2860.39
BLD12PST |  | Water Consumption (m3)
BLD12PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Water Systems | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
BLD12PST |  |  | Total Building | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
BLD12PST |  | Emissions
BLD12PST |  |  | Carbon Equivalent (kg) | 30262.8796 | 33624.9554 | 32102.0878 | 28934.1101 | 10525.0069 | 32924.6475 | 9895.3518 | 24683.5331 | 36626.8769 | 6937.6907 | 47899.3513 | 36126.5092 | 31995.52 | 32877.2794 | 31787.5459 | 30117.8206
BLD12PST |  |  | CO2 (kg) | 70186.59 | 84584.3995 | 75694.8296 | 66271.7973 | 28167.1959 | 78268.7316 | 26571.44 | 56243.3113 | 85901.7414 | 17058.3317 | 111660.3906 | 84968.7887 | 75272.751 | 77628.3362 | 75115.6261 | 77662.9093
BLD12PST |  |  | NOX (kg) | 123.3019 | 110.53 | 127.0938 | 125.0942 | 24.1509 | 127.1921 | 22.8438 | 108.1145 | 148.2784 | 25.1365 | 198.1379 | 145.6223 | 130.5046 | 132.6379 | 128.7551 | 91.545
BLD12PST |  |  | SO2 (kg) | 469.3087 | 472.9577 | 422.662 | 318.6228 | 254.4422 | 528.026 | 229.0858 | 315.3103 | 380.8917 | 61.7002 | 580.6536 | 371.0949 | 202.8122 | 225.2064 | 197.5793 | 440.5206
BLD12PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12PST |  |  | Hg (kg) | 0.0021 | 0.0013 | 0.0011 | 0.0012 | 0.0001 | 0.001 | 0.0001 | 0.0013 | 0.0015 | 0.0002 | 0.0018 | 0.0015 | 0.0015 | 0.0016 | 0.0015 | 0.0015
BLD12PST |  |  | Water for Electricity (m3) | 58.083 | 161.33 | 3122.14 | 566.7416 | 1535.24 | 2633.37 | 1382.21 | 19.6095 | 396.0532 | 815.36 | 133.6663 | 385.8597 | 133.2924 | 5341.92 | 129.8472 | 88.3984
BLD12NEW |  | Program
BLD12NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD12NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD12NEW |  |  | Weighting Factor | 201.9091 | 2559.5418 | 695.7164 | 2316.0945 |  | 1142.2145 | 186.9745 | 2251.0327 | 113.8618 | 294.7673 | 2213.0109 | 774.1455 | 580.2291 | 72.6764 | 77.7964 | 11.2727
BLD12NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD12NEW |  |  | Exterior walls
BLD12NEW | TypeWall |  | Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
BLD12NEW | RvalWall |  | R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
BLD12NEW |  |  | Roof
BLD12NEW | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD12NEW | RvalRoof |  | R-value attic floor (m2·K / W) | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 6.5229 | 6.5229 | 6.5229 | 6.5229
BLD12NEW |  |  | Window
BLD12NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD12NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD12NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BLD12NEW |  |  | Skylights/TDD
BLD12NEW |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD12NEW |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD12NEW |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD12NEW |  |  | Foundation
BLD12NEW |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD12NEW |  |  | Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
BLD12NEW |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD12NEW |  | HVAC
BLD12NEW |  |  | HVAC Sizing
BLD12NEW | HVAC |  | Air Conditioning (kW) | 38.6566 | 36.0325 | 37.2098 | 33.6 | 26.9743 | 28.349 | 26.5499 | 33.7549 | 29.9972 | 27.2727 | 32.9564 | 29.2012 | 32.0788 | 29.0537 | 29.3444 | 26.7576
BLD12NEW |  |  | PSZ-AC:1_COOLC DXCOIL | 9.6595 | 8.7615 | 8.0624 | 8.8038 | 7.2501 | 6.8721 | 5.2359 | 8.311 | 7.5531 | 6.1595 | 8.0913 | 7.2523 | 7.9314 | 6.7071 | 6.2086 | 5.8184
BLD12NEW |  |  | PSZ-AC:2_COOLC DXCOIL | 7.4175 | 6.5834 | 7.7527 | 6.7311 | 5.4317 | 5.639 | 8.0721 | 6.5094 | 5.2103 | 6.7194 | 6.3738 | 5.394 | 6.2216 | 5.899 | 6.3897 | 6.5265
BLD12NEW |  |  | PSZ-AC:3_COOLC DXCOIL | 6.3974 | 6.2333 | 6.1228 | 5.3234 | 4.3144 | 4.7869 | 4.3764 | 5.7847 | 5.4489 | 4.5952 | 5.6451 | 5.2726 | 5.5406 | 5.0791 | 5.4412 | 4.093
BLD12NEW |  |  | PSZ-AC:4_COOLC DXCOIL | 7.767 | 6.955 | 7.7585 | 6.9131 | 5.3116 | 5.79 | 3.3136 | 6.5833 | 5.4518 | 4.5292 | 6.3898 | 5.1686 | 6.2192 | 5.5841 | 5.2619 | 6.2268
BLD12NEW |  |  | PSZ-AC:5_COOLC DXCOIL | 7.4152 | 7.4992 | 7.5134 | 5.8286 | 4.6665 | 5.2609 | 5.552 | 6.5666 | 6.3331 | 5.2694 | 6.4564 | 6.1137 | 6.166 | 5.7844 | 6.0431 | 4.093
BLD12NEW | HEAT |  | Heating (kW) | 50.4968 | 52.8923 | 51.3558 | 49.8258 | 41.8246 | 43.3609 | 42.6961 | 53.4567 | 42.4866 | 45.7119 | 55.3092 | 44.1257 | 55.7513 | 48.9374 | 53.808 | 57.3717
BLD12NEW |  |  | PSZ-AC:1_HEATC | 12.2619 | 13.044 | 11.3748 | 13.0981 | 11.2862 | 10.8629 | 9.0032 | 13.4036 | 11.0348 | 10.8842 | 13.9832 | 11.4401 | 14.1931 | 12.1611 | 12.8233 | 14.0426
BLD12NEW |  |  | PSZ-AC:2_HEATC | 9.5949 | 9.9054 | 10.0731 | 10.153 | 8.5336 | 8.7858 | 12.5212 | 10.6372 | 7.7758 | 11.0579 | 11.1249 | 8.5536 | 11.2326 | 10.1995 | 11.2118 | 13.5366
BLD12NEW |  |  | PSZ-AC:3_HEATC | 8.5187 | 8.8429 | 8.7328 | 7.7694 | 6.5993 | 7.0621 | 6.8557 | 8.9174 | 7.3071 | 7.3939 | 9.1634 | 7.4382 | 9.2493 | 7.9535 | 9.2626 | 8.3328
BLD12NEW |  |  | PSZ-AC:4_HEATC | 10.1849 | 10.5472 | 10.5497 | 10.4639 | 8.3191 | 8.9795 | 5.8282 | 10.7644 | 8.0517 | 8.0587 | 11.1522 | 8.2964 | 11.2251 | 9.8202 | 10.4533 | 13.1269
BLD12NEW |  |  | PSZ-AC:5_HEATC | 9.9364 | 10.5529 | 10.6253 | 8.3416 | 7.0864 | 7.6705 | 8.4878 | 9.7342 | 8.3173 | 8.3172 | 9.8854 | 8.3975 | 9.8513 | 8.8031 | 10.057 | 8.3328
BLD12NEW |  |  | HVAC Efficiency
BLD12NEW |  |  | Air Conditioning (COP)
BLD12NEW | COP |  | PSZ-AC:1_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD12NEW |  |  | PSZ-AC:2_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD12NEW |  |  | PSZ-AC:3_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD12NEW |  |  | PSZ-AC:4_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD12NEW |  |  | PSZ-AC:5_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD12NEW |  |  | Heating Efficiency (%)
BLD12NEW | EffHeat |  | PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12NEW |  |  | PSZ-AC:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12NEW |  |  | PSZ-AC:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12NEW |  |  | PSZ-AC:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12NEW |  |  | PSZ-AC:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD12NEW |  |  | HVAC Control - Economizer
BLD12NEW |  |  | PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12NEW |  |  | PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12NEW |  |  | PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12NEW |  |  | PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12NEW |  |  | PSZ-AC:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD12NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 2.02 | 1.98 | 2.07 | 1.84 | 1.62 | 1.72 | 1.61 | 1.87 | 1.81 | 1.65 | 1.86 | 1.77 | 1.81 | 1.77 | 1.75 | 1.62
BLD12NEW |  |  | PSZ-AC:1_FAN | 0.48 | 0.47 | 0.44 | 0.47 | 0.43 | 0.42 | 0.32 | 0.45 | 0.46 | 0.37 | 0.45 | 0.44 | 0.44 | 0.41 | 0.38 | 0.35
BLD12NEW |  |  | PSZ-AC:2_FAN | 0.38 | 0.36 | 0.4 | 0.37 | 0.33 | 0.34 | 0.49 | 0.36 | 0.31 | 0.41 | 0.36 | 0.33 | 0.35 | 0.36 | 0.35 | 0.39
BLD12NEW |  |  | PSZ-AC:3_FAN | 0.35 | 0.34 | 0.36 | 0.3 | 0.26 | 0.29 | 0.26 | 0.33 | 0.33 | 0.28 | 0.33 | 0.32 | 0.32 | 0.31 | 0.33 | 0.25
BLD12NEW |  |  | PSZ-AC:4_FAN | 0.4 | 0.39 | 0.42 | 0.38 | 0.32 | 0.35 | 0.2 | 0.37 | 0.33 | 0.27 | 0.36 | 0.31 | 0.35 | 0.34 | 0.32 | 0.38
BLD12NEW |  |  | PSZ-AC:5_FAN | 0.41 | 0.42 | 0.45 | 0.32 | 0.28 | 0.32 | 0.34 | 0.36 | 0.38 | 0.32 | 0.36 | 0.37 | 0.35 | 0.35 | 0.37 | 0.25
BLD12NEW |  | Utility Costs
BLD12NEW |  |  | Electric Utility Rates
BLD12NEW |  |  | Average Annual Rate ($/kWh) | 0.10232 | 0.119 | 0.12121 | 0.11748 | 0.12765 | 0.10058 | 0.15966 | 0.074943 | 0.075236 | 0.073211 | 0.064125 | 0.075276 | 0.074878 | 0.075544 | 0.074722 | 0.10025
BLD12NEW |  |  | Total Cost ($/m2) | 16.32 | 17.44 | 18.93 | 15.41 | 15.7 | 13.52 | 18.88 | 9.68 | 9.6 | 8.65 | 8.13 | 9.29 | 9.42 | 9.19 | 9.09 | 12.02
BLD12NEW |  |  | Gas Utility Rates
BLD12NEW |  |  | Average Annual Rate ($/MJ) | 0.011467 | 0.0081068 | 0.0084069 | 0.0099266 | 0.0084397 | 0.0078851 | 0.0086046 | 0.0097332 | 0.0069517 | 0.008434 | 0.0083434 | 0.0069201 | 0.0079145 | 0.008049 | 0.0078859 | 0.004113
BLD12NEW |  |  | Total Cost ($/m2) | 0.23 | 0.43 | 0.32 | 0.61 | 0.2 | 0.33 | 0.39 | 1.06 | 0.5 | 0.87 | 1.34 | 0.78 | 1.69 | 1.4 | 2.02 | 2.08
BLD12NEW |  |  | Total Utility Costs
BLD12NEW |  |  | Cost Intensity ($/m2) | 16.55 | 17.87 | 19.25 | 16.02 | 15.9 | 13.84 | 19.27 | 10.74 | 10.09 | 9.52 | 9.46 | 10.07 | 11.1 | 10.59 | 11.11 | 14.1
BLD12NEW |  | Energy - End Uses
BLD12NEW |  |  | Electricity (kWh)
BLD12NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Cooling | 19244.4444 | 13258.3333 | 16669.4444 | 6852.7778 | 3986.1111 | 8980.5556 | 1663.8889 | 5491.6667 | 5152.7778 | 1388.8889 | 4158.3333 | 3138.8889 | 3577.7778 | 2080.5556 | 1575 | 547.2222
BLD12NEW |  |  | Interior Lighting | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222 | 15747.2222
BLD12NEW |  |  | Exterior Lighting | 10066.6667 | 10063.8889 | 10061.1111 | 10058.3333 | 10052.7778 | 10050 | 10055.5556 | 10047.2222 | 10052.7778 | 10033.3333 | 10050 | 10044.4444 | 10044.4444 | 10041.6667 | 10036.1111 | 9975
BLD12NEW |  |  | Interior Equipment | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444 | 24369.4444
BLD12NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Fans | 12083.3333 | 11472.2222 | 12997.2222 | 10011.1111 | 8716.6667 | 9547.2222 | 8622.2222 | 10358.3333 | 9894.4444 | 8888.8889 | 10463.8889 | 9761.1111 | 10541.6667 | 9963.8889 | 10438.8889 | 10661.1111
BLD12NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Total End Uses | 81508.3333 | 74908.3333 | 79841.6667 | 67036.1111 | 62869.4444 | 68691.6667 | 60455.5556 | 66013.8889 | 65213.8889 | 60425 | 64786.1111 | 63061.1111 | 64280.5556 | 62202.7778 | 62166.6667 | 61297.2222
BLD12NEW |  |  | Gas (MJ)
BLD12NEW |  |  | Heating | 150 | 16750 | 8940 | 20650 | 1210 | 10620 | 11670 | 44500 | 25220 | 41040 | 70300 | 46040 | 97070 | 76960 | 118920 | 245480
BLD12NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Water Systems | 10180 | 10580 | 10350 | 10970 | 10890 | 10630 | 11220 | 11270 | 11210 | 11420 | 11530 | 11520 | 11760 | 11800 | 12140 | 12590
BLD12NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Total End Uses | 10340 | 27330 | 19290 | 31610 | 12100 | 21240 | 22890 | 55770 | 36430 | 52470 | 81830 | 57560 | 108830 | 88760 | 131060 | 258070
BLD12NEW |  |  | Purchased Cooling (MJ)
BLD12NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Purchased Heating (MJ)
BLD12NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Total Building (MJ) | 303770 | 297000 | 306720 | 272940 | 238430 | 268530 | 240530 | 293420 | 271210 | 270000 | 315070 | 284570 | 340240 | 312690 | 354860 | 478750
BLD12NEW |  | Energy - End Use Intensities
BLD12NEW |  |  | Electricity (MJ/m2)
BLD12NEW |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Cooling (elec) | 135.5349 | 93.3759 | 117.3996 | 48.2628 | 28.0734 | 63.2483 | 11.7184 | 38.6767 | 36.29 | 9.7817 | 29.2863 | 22.1066 | 25.1976 | 14.6529 | 11.0924 | 3.854
BLD12NEW |  |  | Interior Lighting (elec) | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046 | 110.9046
BLD12NEW |  |  | Exterior Lighting (elec) | 70.8976 | 70.878 | 70.8584 | 70.8389 | 70.7997 | 70.7802 | 70.8193 | 70.7606 | 70.7997 | 70.6628 | 70.7802 | 70.7411 | 70.7411 | 70.7215 | 70.6824 | 70.252
BLD12NEW |  |  | Interior Equipment (elec) | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292 | 171.6292
BLD12NEW |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Fans (elec) | 85.1006 | 80.7966 | 91.5369 | 70.5063 | 61.3898 | 67.2392 | 60.7246 | 72.9517 | 69.6846 | 62.6027 | 73.6951 | 68.7456 | 74.2429 | 70.1737 | 73.5191 | 75.0841
BLD12NEW |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Total End Uses | 574.0473 | 527.5648 | 562.3093 | 472.1222 | 442.7772 | 483.782 | 425.7767 | 464.9229 | 459.2887 | 425.5615 | 456.2759 | 444.1271 | 452.7154 | 438.082 | 437.8277 | 431.7044
BLD12NEW |  |  | Gas (MJ/m2)
BLD12NEW |  |  | Heating (gas) | 0.29345 | 32.7686 | 17.4896 | 40.3983 | 2.3672 | 20.7763 | 22.8304 | 87.0569 | 49.3388 | 80.288 | 137.5303 | 90.0696 | 189.9014 | 150.5595 | 232.6473 | 480.241
BLD12NEW |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Water Systems (gas) | 19.9155 | 20.698 | 20.2481 | 21.461 | 21.3045 | 20.7958 | 21.9501 | 22.0479 | 21.9305 | 22.3413 | 22.5565 | 22.537 | 23.0065 | 23.0847 | 23.7499 | 24.6303
BLD12NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Total End Uses | 20.2285 | 53.4666 | 37.7377 | 61.8397 | 23.6716 | 41.5525 | 44.7805 | 109.1048 | 71.2693 | 102.6489 | 160.0869 | 112.6066 | 212.9079 | 173.6443 | 256.3972 | 504.8713
BLD12NEW |  |  | Purchased Cooling (MJ/m2)
BLD12NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Purchased Heating (MJ/m2)
BLD12NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Total Building (MJ/m2) | 594.2758 | 581.0314 | 600.047 | 533.962 | 466.4489 | 525.3345 | 470.5572 | 574.0277 | 530.5775 | 528.2103 | 616.3823 | 556.7141 | 665.6233 | 611.7263 | 694.2249 | 936.5952
BLD12NEW |  | Peak Energy Demand
BLD12NEW |  |  | Electricity Peak Demand (kW)
BLD12NEW |  |  | Jan | 17.4675 | 15.6119 | 14.4383 | 12.9281 | 14.4721 | 14.4485 | 14.0591 | 14.3769 | 12.5973 | 14.1141 | 14.3576 | 14.2492 | 14.3121 | 14.2389 | 14.2205 | 14.078
BLD12NEW |  |  | Feb | 17.9631 | 15.9495 | 15.2949 | 12.8853 | 13.8892 | 13.0099 | 13.7082 | 12.2218 | 13.283 | 12.0857 | 14.3576 | 12.3216 | 12.0167 | 12.2933 | 11.9634 | 14.078
BLD12NEW |  |  | Mar | 18.3376 | 15.8942 | 17.6902 | 13.9691 | 13.7565 | 13.9086 | 12.7809 | 13.8427 | 13.4206 | 13.0001 | 13.0806 | 13.4128 | 12.4088 | 13.1829 | 12.0293 | 14.078
BLD12NEW |  |  | Apr | 18.8747 | 17.305 | 17.9055 | 15.5994 | 14.5698 | 16.2301 | 13.8064 | 14.3945 | 14.8646 | 12.6295 | 13.3987 | 14.1643 | 13.2652 | 12.7746 | 12.4436 | 11.8457
BLD12NEW |  |  | May | 19.7251 | 20.0651 | 20.8081 | 17.2441 | 14.6337 | 17.8225 | 13.9985 | 16.0811 | 16.3283 | 14.0774 | 15.8276 | 15.2713 | 15.8928 | 13.9668 | 14.1033 | 13.0005
BLD12NEW |  |  | Jun | 20.9769 | 20.294 | 24.3027 | 18.4107 | 14.5615 | 20.6495 | 14.4378 | 19.2562 | 17.776 | 14.7443 | 18.2704 | 16.5176 | 18.0921 | 16.6642 | 15.9384 | 14.3041
BLD12NEW |  |  | Jul | 20.4669 | 20.8989 | 23.9188 | 19.9352 | 15.3704 | 20.3336 | 15.5513 | 19.9544 | 18.4247 | 15.8437 | 18.9933 | 17.5718 | 18.2264 | 17.0713 | 17.1777 | 14.4725
BLD12NEW |  |  | Aug | 20.7191 | 20.7884 | 23.9145 | 18.3682 | 16.0878 | 19.7378 | 14.7663 | 19.7093 | 18.2124 | 15.5498 | 18.7259 | 17.6932 | 18.0008 | 16.5206 | 16.4536 | 14.1958
BLD12NEW |  |  | Sep | 20.0729 | 19.7515 | 21.876 | 17.682 | 16.176 | 19.2346 | 16.9611 | 17.4155 | 16.2796 | 15.2957 | 16.6874 | 15.7968 | 16.2798 | 15.1404 | 15.1449 | 11.9952
BLD12NEW |  |  | Oct | 19.5894 | 18.6125 | 18.5749 | 16.2083 | 15.3307 | 16.5363 | 14.466 | 15.7302 | 14.9555 | 13.1977 | 14.7439 | 14.9807 | 13.6542 | 14.2389 | 12.8986 | 14.078
BLD12NEW |  |  | Nov | 18.4045 | 16.5974 | 16.7981 | 13.9185 | 15.6108 | 15.4931 | 14.5547 | 15.0477 | 14.4752 | 14.1141 | 14.3576 | 14.3862 | 14.3121 | 14.2389 | 14.2205 | 14.078
BLD12NEW |  |  | Dec | 17.39 | 15.6049 | 14.1604 | 12.6153 | 15.2141 | 14.812 | 14.1401 | 14.3769 | 14.4109 | 14.1141 | 14.3576 | 14.2853 | 14.3121 | 14.2389 | 14.2205 | 14.078
BLD12NEW |  |  | Time of Peak Electrical Demand
BLD12NEW |  |  | Jan | 23-JAN-15:00 | 03-JAN-13:00 | 27-JAN-14:00 | 23-JAN-16:30 | 12-JAN-16:00 | 18-JAN-16:49 | 02-JAN-16:00 | 02-JAN-16:49 | 27-JAN-15:09 | 02-JAN-16:30 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 04-JAN-16:49 | 02-JAN-16:30 | 02-JAN-08:09
BLD12NEW |  |  | Feb | 22-FEB-15:00 | 23-FEB-15:09 | 28-FEB-16:30 | 22-FEB-15:00 | 13-FEB-11:00 | 27-FEB-15:00 | 15-FEB-15:00 | 16-FEB-13:20 | 14-FEB-15:50 | 21-FEB-13:20 | 01-FEB-16:00 | 07-FEB-13:20 | 22-FEB-13:20 | 03-FEB-14:30 | 22-FEB-14:20 | 01-FEB-08:09
BLD12NEW |  |  | Mar | 13-MAR-15:50 | 28-MAR-14:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:00 | 31-MAR-15:00 | 01-MAR-13:00 | 10-MAR-10:00 | 02-MAR-15:30 | 29-MAR-15:50 | 31-MAR-14:00 | 30-MAR-15:00 | 23-MAR-15:50 | 30-MAR-15:00 | 22-MAR-13:00 | 01-MAR-08:09
BLD12NEW |  |  | Apr | 03-APR-14:39 | 21-APR-15:30 | 26-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:39 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:00 | 19-APR-15:00 | 28-APR-15:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:30 | 25-APR-13:30
BLD12NEW |  |  | May | 24-MAY-14:00 | 18-MAY-15:30 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-08:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
BLD12NEW |  |  | Jun | 28-JUN-14:00 | 13-JUN-15:39 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-15:30 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 30-JUN-14:00 | 14-JUN-15:00 | 21-JUN-15:00
BLD12NEW |  |  | Jul | 13-JUL-15:20 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-15:00 | 24-JUL-14:00 | 03-JUL-14:00 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
BLD12NEW |  |  | Aug | 21-AUG-15:09 | 31-AUG-15:00 | 01-AUG-15:00 | 17-AUG-15:30 | 08-AUG-09:00 | 04-AUG-15:00 | 15-AUG-12:09 | 09-AUG-14:00 | 01-AUG-14:00 | 07-AUG-15:20 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-13:00
BLD12NEW |  |  | Sep | 11-SEP-14:00 | 15-SEP-14:00 | 11-SEP-15:00 | 11-SEP-13:00 | 25-SEP-12:09 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-15:20 | 29-SEP-14:39 | 01-SEP-15:00 | 27-SEP-14:00 | 06-SEP-14:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 07-SEP-15:00
BLD12NEW |  |  | Oct | 06-OCT-15:00 | 06-OCT-15:00 | 02-OCT-14:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 31-OCT-12:00 | 12-OCT-14:00 | 13-OCT-14:39 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-14:00 | 06-OCT-14:00 | 30-OCT-07:10 | 06-OCT-14:00 | 03-OCT-07:10
BLD12NEW |  |  | Nov | 07-NOV-14:00 | 03-NOV-14:30 | 13-NOV-15:30 | 22-NOV-14:00 | 09-NOV-16:00 | 10-NOV-16:40 | 14-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 06-NOV-16:49 | 06-NOV-16:40 | 10-NOV-16:49 | 06-NOV-16:00 | 08-NOV-16:00 | 06-NOV-16:49 | 01-NOV-07:10
BLD12NEW |  |  | Dec | 15-DEC-15:30 | 19-DEC-15:20 | 11-DEC-15:00 | 05-DEC-14:39 | 18-DEC-16:49 | 05-DEC-16:30 | 07-DEC-16:49 | 01-DEC-16:40 | 05-DEC-16:49 | 01-DEC-16:19 | 01-DEC-16:19 | 21-DEC-16:40 | 01-DEC-16:30 | 11-DEC-16:40 | 01-DEC-16:19 | 01-DEC-08:09
BLD12NEW |  | Source Energy
BLD12NEW |  |  | Total Source Energy (GJ) | 984.6 | 1009.3 | 930.21 | 846.36 | 713.71 | 907.75 | 698.59 | 910.74 | 818.77 | 436.24 | 916.41 | 816.09 | 914.2 | 875.3 | 912.31 | 1070.06
BLD12NEW |  |  | Total Source Energy (MJ/m2) | 1926.23 | 1974.53 | 1819.81 | 1655.78 | 1396.27 | 1775.87 | 1366.69 | 1781.72 | 1601.79 | 853.43 | 1792.82 | 1596.56 | 1788.5 | 1712.39 | 1784.79 | 2093.41
BLD12NEW |  | Water Consumption (m3)
BLD12NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Water Systems | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
BLD12NEW |  |  | Total Building | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63 | 17.63
BLD12NEW |  | Emissions
BLD12NEW |  |  | Carbon Equivalent (kg) | 22540.2466 | 25479.6312 | 24450.2121 | 21219.8225 | 7565.5739 | 23550.8827 | 7477.9383 | 18819.901 | 27297.2424 | 5347.2084 | 36016.9536 | 26797.7287 | 23965.3687 | 24331.565 | 23642.2135 | 21902.3134
BLD12NEW |  |  | CO2 (kg) | 52300.1081 | 64122.9355 | 57686.5232 | 48513.7168 | 20246.6813 | 55980.0262 | 20055.3672 | 42854.6113 | 63972.5557 | 13188.2282 | 83959.6279 | 63021.6271 | 56395.3534 | 57493.7242 | 55884.3769 | 56653.5438
BLD12NEW |  |  | NOX (kg) | 91.7758 | 83.7048 | 96.7132 | 91.9948 | 17.3594 | 90.9929 | 17.225 | 82.5121 | 110.6352 | 19.2797 | 148.9889 | 108.0348 | 97.7119 | 98.0463 | 95.7175 | 66.3381
BLD12NEW |  |  | SO2 (kg) | 348.8935 | 357.3241 | 321.0653 | 235.3073 | 182.9468 | 377.8615 | 175.9256 | 240.992 | 284.791 | 46.7186 | 436.6359 | 275.3847 | 151.7417 | 166.1106 | 146.7554 | 312.1014
BLD12NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD12NEW |  |  | Hg (kg) | 0.0016 | 0.001 | 0.0009 | 0.0009 | 0.0001 | 0.0007 | 0.0001 | 0.001 | 0.0011 | 0.0002 | 0.0013 | 0.0011 | 0.0011 | 0.0012 | 0.0011 | 0.0011
BLD12NEW |  |  | Water for Electricity (m3) | 43.18 | 121.886 | 2371.65 | 418.5502 | 1103.85 | 1884.47 | 1061.47 | 14.9876 | 296.1286 | 617.3613 | 100.5135 | 286.3415 | 99.7275 | 3940.13 | 96.4459 | 62.6271

## Picture
DOE Commercial Building Benchmark - Small Office

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
[5 empty] | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
[5 empty] | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
|  | BLDG_OCC_SCH | Fraction | Through 12/31 | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1 | 47.4 | 2471.57
SchOcc | WD |  |  |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1
| Sat |  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 55.3 | 2883.5
| Sat |  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 78.95 | 4116.68
| Sat |  |  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  |  |  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  |  |  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 597.6 | 3596.4 | 187526.57
| Sat |  |  |  | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 608.4
| Sun |  |  |  | Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 2743.2 | 143038.29
| Sat |  |  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 439.2
[5 empty] | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
| Sun |  |  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  | MinOA_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
[5 empty] | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
|  | HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
[5 empty] | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchGas | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 29.42 | 1534.04
| Sat |  |  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
| Sun |  |  |  | Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
|  | Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
|  | Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
|  | Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600