## 1
1 | Building Summary Warehouse pre-1980 construction
UWG |  |  | Value | Value | Value
areaFloor |  | Total Floor Area (m2) | 4835.13 | 4835.13 | 4835.13
nFloor |  | Number of Floors | 1 | 1 | 1
glazing |  | Total | 0.0058 | 0.0058 | 0.0058
hCeiling |  | Floor to Ceiling Height (m) | 8.53 | 8.53 | 8.53
areaWall |  | Gross Dimensions - Total Area (m2) | 1977.67 | 1977.67 | 1977.67
ver2hor |  | Wall to Skin Ratio | 0.35192 | 0.35192 | 0.35192
areaRoof |  | Gross Dimensions - Total Area (m2) | 4598.25 | 4598.25 | 4598.25
areaWindow |  | Total Area (m2) | 17.66 | 17.66 | 17.66

## 2
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD16PRE | Total | Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.9923 | 17.66 |  | 5 | 6.6341 | 2.1791 | 0 | 0 | 10 | 0.24809 | 1199.5625 |  | 0.73639
BLD16PST | Total | Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.9923 | 17.66 |  | 5 | 6.6341 | 2.1791 | 0 | 0 | 10 | 0.24809 | 1199.5625 |  | 0.73639
BLD16NEW | Total | Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.9923 | 17.66 |  | 5 | 11.344 | 2.1791 | 0 | 0 | 10 | 0.24809 | 1199.5625 |  | 0.19637

## 3
3 |  | Location Summary
BLD | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD16PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD16PRE | TypeWall |  | Construction Type | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall
BLD16PRE | RvalWall |  | R-value (m2·K / W) | 0.57405 | 0.57405 | 0.57405 | 0.59137 | 0.57405 | 0.57405 | 0.59453 | 0.79808 | 0.7657 | 0.815 | 0.93721 | 0.90253 | 1.0235 | 1.0235 | 1.1038 | 1.218
BLD16PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD16PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD16PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD16PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD16PRE | HVAC |  | Air Conditioning (kW) | 105.8732 | 158.8848 | 161.8592 | 195.5053 | 90.1303 | 136.9651 | 91.684 | 211.5131 | 181.0061 | 129.7417 | 277.3309 | 249.871 | 311.9059 | 263.8501 | 332.9035 | 295.469
BLD16PRE | HEAT |  | Heating (kW) | 137.849 | 303.087 | 174.5427 | 404.073 | 151.5929 | 276.587 | 178.9506 | 476.1077 | 384.0059 | 312.7043 | 667.2273 | 541.8259 | 772.0495 | 737.9708 | 824.1667 | 1172.5836
BLD16PRE | COP |  | Air Conditioning (COP) | 3.2995 | 3.286 | 3.2806 | 3.2801 | 3.2882 | 3.2805 | 3.288 | 3.2784 | 3.2761 | 3.2793 | 3.1586 | 3.269 | 3.1573 | 3.1565 | 3.1556 | 3.1581
BLD16PRE | EffHeat |  | Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD16PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 5.14 | 9.07 | 7.71 | 12.22 | 4.7 | 9.03 | 5.67 | 13.72 | 13.59 | 9.35 | 19.19 | 18.75 | 22.24 | 23.83 | 24.18 | 32.89
BLD16PST | TypeWall |  | Construction Type | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall
BLD16PST | RvalWall |  | R-value (m2·K / W) | 0.2291 | 0.98232 | 0.5423 | 1.1628 | 0.60901 | 0.90909 | 1.1628 | 1.7889 | 1.5699 | 1.7241 | 1.9569 | 1.9569 | 2.5189 | 2.2523 | 2.849 | 3.7175
BLD16PST | TypeRoof |  | Construction Type | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof
BLD16PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD16PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD16PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
BLD16PST | HVAC |  | Air Conditioning (kW) | 109.4302 | 146.4754 | 129.9179 | 178.3724 | 90.3996 | 128.2802 | 85.0889 | 193.622 | 170.1054 | 120.8683 | 257.905 | 232.5398 | 289.3057 | 243.6532 | 306.7005 | 269.6977
BLD16PST | HEAT |  | Heating (kW) | 150.4944 | 272.1712 | 168.8369 | 361.9632 | 151.7525 | 242.2456 | 168.3537 | 428.3134 | 340.8525 | 284.0629 | 615.8139 | 486.2921 | 712.1072 | 684.0542 | 754.9443 | 1066.1421
BLD16PST | COP |  | Air Conditioning (COP) | 3.3008 | 3.2867 | 3.2903 | 3.2795 | 3.2879 | 3.2791 | 3.3762 | 3.278 | 3.2727 | 3.2766 | 3.2415 | 3.2665 | 3.1563 | 3.2702 | 3.1545 | 3.157
BLD16PST | EffHeat |  | Heating Efficiency (%) | 0.78372 | 0.78232 | 0.78333 | 0.78192 | 0.78325 | 0.78251 | 0.78302 | 0.7817 | 0.78189 | 0.78212 | 0.78144 | 0.78156 | 0.78134 | 0.78135 | 0.78131 | 0.78117
BLD16PST | Fan |  | Fan Max Flow Rate (m3/s ) | 5.31 | 8.13 | 6.38 | 10.9 | 4.7 | 7.89 | 5.3 | 12.27 | 12.01 | 8.46 | 17.63 | 16.75 | 20.39 | 21.98 | 22.03 | 29.73
BLD16NEW | TypeWall |  | Construction Type | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall | Metal building wall
BLD16NEW | RvalWall |  | R-value (m2·K / W) | 0.2291 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 1.1223 | 1.1223 | 1.1223 | 1.2407 | 1.2407 | 1.3661 | 1.3661 | 1.3661 | 1.3661
BLD16NEW | TypeRoof |  | Construction Type | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof | Metal building roof
BLD16NEW | RvalRoof |  | R-value (m2·K / W) | 0.18847 | 1.0515 | 1.0515 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8657 | 1.8657 | 1.8657 | 1.8657 | 1.8116 | 2.5
BLD16NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835
BLD16NEW | SHGC |  | SHGC | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BLD16NEW | HVAC |  | Air Conditioning (kW) | 357.2415 | 121.4741 | 130.6539 | 110.7776 | 57.0132 | 87.1247 | 57.1165 | 116.1541 | 97.9004 | 71.2217 | 149.1937 | 127.1999 | 166.502 | 135.5043 | 178.3224 | 150.1451
BLD16NEW | HEAT |  | Heating (kW) | 172.0249 | 194.267 | 133.488 | 216.7679 | 114.7011 | 154.8652 | 127.7757 | 247.6128 | 209.5607 | 160.4572 | 345.8662 | 287.6877 | 401.336 | 395.5533 | 433.9112 | 565.6953
BLD16NEW | COP |  | Air Conditioning (COP) | 3.1529 | 3.2728 | 3.2936 | 3.2812 | 3.3893 | 3.3724 | 3.39 | 3.278 | 3.2853 | 3.3834 | 3.2737 | 3.278 | 3.2708 | 3.2795 | 3.268 | 3.2801
BLD16NEW | EffHeat |  | Heating Efficiency (%) | 0.78277 | 0.78246 | 0.78299 | 0.78247 | 0.79316 | 0.78299 | 0.78319 | 0.78215 | 0.78233 | 0.78278 | 0.7818 | 0.78193 | 0.78165 | 0.78164 | 0.78159 | 0.78148
BLD16NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 19.57 | 6.6 | 7.08 | 6.41 | 3.6 | 5.37 | 3.88 | 6.9 | 7.25 | 4.74 | 9.54 | 9.65 | 11.05 | 12.28 | 12.19 | 15.05

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 10.1 | 56.3 | 2935.64
| Sat |  |  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.4
| Sun |  |  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 9.8 | 54.22 | 2827.19
| Sat |  |  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82
| Sun |  |  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35.2 | 1835.43
| Sat |  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2
| Sun |  |  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 660 | 3972 | 207111.43
| Sat |  |  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 672
| Sun |  |  |  | Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 432.5 | 2584 | 134737.14
| Sat |  |  |  | Sat | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 421.5
| Sun |  |  |  | Other | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
SchGas | WD |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sat |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchSWH | WD |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sat |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## BuildingSummary
Building Summary Warehouse pre-1980 construction
UWG |  |  | Value | Value | Value
Program
|  | Building Name | Warehouse Reference Building pre-1980 construction | Warehouse Reference Building post-1980 construction | Warehouse Reference Building new construction 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Nonrefrigerated warehouse | Nonrefrigerated warehouse | Nonrefrigerated warehouse
Form
areaFloor |  | Total Floor Area (m2) | 4835.13 | 4835.13 | 4835.13
|  | Building Shape | Rectangle | Rectangle | Rectangle
|  | Aspect Ratio | 0.45 | 0.45 | 0.45
nFloor |  | Number of Floors | 1 | 1 | 1
Window Fraction (Window to Wall Ratio)
|  | South | 0.0286 | 0.0286 | 0.0286
|  | East | 0 | 0 | 0
|  | North | 0 | 0 | 0
|  | West | 0.0076 | 0.0076 | 0.0076
glazing |  | Total | 0.0058 | 0.0058 | 0.0058
Skylight/TDD Percentage
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | Bulk storage, fine storage, office | Bulk storage, fine storage, office | Bulk storage, fine storage, office
hCeiling |  | Floor to Ceiling Height (m) | 8.53 | 8.53 | 8.53
|  | Floor to Floor Height (m) | 8.53 | 8.53 | 8.53
|  | Roof type | Built-up flat roof, insulation entirely above deck | Metal building roof | Metal building roof
Fabric
Exterior walls
|  | Construction Type | Metal building wall | Metal building wall | Metal building wall
areaWall |  | Gross Dimensions - Total Area (m2) | 1977.67 | 1977.67 | 1977.67
|  | Net Dimensions - Total Area (m2) | 1324.84 | 1324.84 | 1324.84
ver2hor |  | Wall to Skin Ratio | 0.35192 | 0.35192 | 0.35192
Roof
|  | Construction Type | IEAD | Metal building roof | Metal building roof
areaRoof |  | Gross Dimensions - Total Area (m2) | 4598.25 | 4598.25 | 4598.25
|  | Net Dimensions - Total Area (m2) | 4598.25 | 4598.25 | 4598.25
|  | Roof to Skin Ratio | 0.64808 | 0.64808 | 0.64808
Window Dimensions (m2)
|  | South | 11.15 | 11.15 | 11.15
|  | East | 0 | 0 | 0
|  | North | 0 | 0 | 0
|  | West | 6.51 | 6.51 | 6.51
areaWindow |  | Total Area (m2) | 17.66 | 17.66 | 17.66
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
|  | Foundation Type | Mass Floor | Mass Floor | Mass Floor
|  | Construction | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade
|  | Dimensions - Total Area (m2) | 4598.25 | 4598.25 | 4598.25
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
|  | Dimensions - Total Area (m2) | 539.71 | 539.71 | 539.71
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 9670.26 | 9670.26 | 9670.26
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 0.74 | 0.74 | 0.2
HVAC
|  | System Type | PSZ-AC office, semi-conditioned storage | PSZ-AC office, semi-conditioned storage | PSZ-AC office, semi-conditioned storage
|  | Heating Type | Gas furnace office, gas unit heaters storage | Gas furnace office, gas unit heaters storage | Gas furnace office, gas unit heaters storage
|  | Cooling Type | PACU office | PACU office | PACU office
|  | Fan Control | SZ CAV | SZ CAV | SZ CAV
Service Water Heating
|  | SWH Type | n/a | n/a | n/a
|  | Fuel | n/a | n/a | n/a
|  | Thermal Efficiency (%) | n/a | n/a | n/a
|  | Temperature Setpoint (ºC ) | n/a | n/a | n/a
|  | Water Consumption (m3 ) | n/a | n/a | n/a

## ZoneSummary
Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
|  | Office | Yes | 1 | 236.88 | 1010.76 | 4.267 | 149.5601 | 17.66 | 47.376 | 5 | 21.6974 | 8.0729 |  |  | 10 |  | 50 |  | 0.60391
|  | FineStorage | Yes | 1 | 1393.41 | 10880.57 | 7.8086 | 760.8007 | 0 |  | 0 | 11.6478 | 0 |  |  |  | 0.25 | 348.3525 |  | 0.80806
|  | BulkStorage | Yes | 1 | 3204.84 | 27350.07 | 8.534 | 1586.6315 | 0 |  | 0 | 3.3409 | 2.691 |  |  |  | 0.25 | 801.21 |  | 0.71502
BLD16PRE | Total | Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.9923 | 17.66 |  | 5 | 6.6341 | 2.1791 | 0 |  |  | 0.24809 | 1199.5625 |  | 0.73639
|  | Office | Yes | 1 | 236.88 | 1010.76 | 4.267 | 149.5601 | 17.66 | 47.376 | 5 | 21.6974 | 8.0729 |  |  | 10 |  | 50 |  | 0.60391
|  | FineStorage | Yes | 1 | 1393.41 | 10880.57 | 7.8086 | 760.8007 | 0 |  | 0 | 11.6478 | 0 |  |  |  | 0.25 | 348.3525 |  | 0.80806
|  | BulkStorage | Yes | 1 | 3204.84 | 27350.07 | 8.534 | 1586.6315 | 0 |  | 0 | 3.3409 | 2.691 |  |  |  | 0.25 | 801.21 |  | 0.71502
BLD16PST | Total | Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.9923 | 17.66 |  | 5 | 6.6341 | 2.1791 | 0 |  |  | 0.24809 | 1199.5625 |  | 0.73639
|  | Office | Yes | 1 | 236.88 | 1010.76 | 4.267 | 149.5601 | 17.66 | 47.376 | 5 | 11.8403 | 8.0729 |  |  | 10 |  | 50 |  | 0.16104
|  | FineStorage | Yes | 1 | 1393.41 | 10880.57 | 7.8086 | 760.8007 | 0 |  | 0 | 15.0695 | 0 |  |  |  | 0.25 | 348.3525 |  | 0.21548
|  | BulkStorage | Yes | 1 | 3204.84 | 27350.07 | 8.534 | 1586.6315 | 0 |  | 0 | 9.6875 | 2.691 |  |  |  | 0.25 | 801.21 |  | 0.19067
BLD16NEW | Total | Total Conditioned Zones |  |  | 4835.13 | 39241.4 |  | 2496.9923 | 17.66 |  | 5 | 11.344 | 2.1791 |  |  |  | 0.24809 | 1199.5625 |  | 0.19637

## LocationSummary
Location Summary
BLD | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD16PRE |  | Program
BLD16PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD16PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD16PRE |  |  | Weighting Factor
BLD16PRE |  | Fabric
BLD16PRE |  |  | Exterior walls
BLD16PRE | TypeWall |  | Construction Type | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall
BLD16PRE | RvalWall |  | R-value (m2·K / W) | 0.57405 | 0.57405 | 0.57405 | 0.59137 | 0.57405 | 0.57405 | 0.59453 | 0.79808 | 0.7657 | 0.815 | 0.93721 | 0.90253 | 1.0235 | 1.0235 | 1.1038 | 1.218
BLD16PRE |  |  | Roof
BLD16PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD16PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD16PRE |  |  | Window
BLD16PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD16PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD16PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD16PRE |  |  | Skylights/TDD
BLD16PRE |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD16PRE |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD16PRE |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD16PRE |  |  | Foundation
BLD16PRE |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD16PRE |  |  | Construction | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade
BLD16PRE |  |  | R-value (m2·K / W) | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809
BLD16PRE |  | HVAC
BLD16PRE |  |  | HVAC Sizing
BLD16PRE | HVAC |  | Air Conditioning (kW) | 105.8732 | 158.8848 | 161.8592 | 195.5053 | 90.1303 | 136.9651 | 91.684 | 211.5131 | 181.0061 | 129.7417 | 277.3309 | 249.871 | 311.9059 | 263.8501 | 332.9035 | 295.469
BLD16PRE |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 27.248 | 32.9452 | 30.3039 | 36.2581 | 19.4417 | 25.595 | 19.6895 | 37.9489 | 30.93 | 23.6698 | 46.662 | 36.0606 | 50.0172 | 41.1476 | 50.0633 | 48.9196
BLD16PRE |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 78.6252 | 125.9396 | 131.5553 | 159.2472 | 70.6886 | 111.3702 | 71.9944 | 173.5643 | 150.0761 | 106.0719 | 230.6689 | 213.8104 | 261.8887 | 222.7025 | 282.8402 | 246.5494
BLD16PRE | HEAT |  | Heating (kW) | 137.849 | 303.087 | 174.5427 | 404.073 | 151.5929 | 276.587 | 178.9506 | 476.1077 | 384.0059 | 312.7043 | 667.2273 | 541.8259 | 772.0495 | 737.9708 | 824.1667 | 1172.5836
BLD16PRE |  |  | BULKSTORAGE UNIT HEATER COIL | 39.3476 | 111.5083 | 35.0601 | 172.4346 | 39.2079 | 97.4243 | 37.1186 | 217.6959 | 166.0511 | 117.8466 | 334.185 | 260.6949 | 398.2948 | 380.4253 | 430.388 | 644.5138
BLD16PRE |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 23.2358 | 34.7697 | 27.9385 | 39.8129 | 24.8557 | 33.2005 | 28.4218 | 41.8491 | 36.8547 | 33.9521 | 49.6677 | 43.1285 | 54.2757 | 52.1468 | 56.0797 | 70.7263
BLD16PRE |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 75.2655 | 156.8091 | 111.5441 | 191.8255 | 87.5293 | 145.9623 | 113.4103 | 216.5627 | 181.1002 | 160.9056 | 283.3746 | 238.0026 | 319.479 | 305.3987 | 337.699 | 457.3434
BLD16PRE |  |  | HVAC Efficiency
BLD16PRE | COP |  | Air Conditioning (COP) | 3.2995 | 3.286 | 3.2806 | 3.2801 | 3.2882 | 3.2805 | 3.288 | 3.2784 | 3.2761 | 3.2793 | 3.1586 | 3.269 | 3.1573 | 3.1565 | 3.1556 | 3.1581
BLD16PRE |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3 | 3.3 | 3.3
BLD16PRE |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.13 | 3.23 | 3.13 | 3.13 | 3.13 | 3.13
BLD16PRE | EffHeat |  | Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD16PRE |  |  | BULKSTORAGE UNIT HEATER COIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD16PRE |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD16PRE |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD16PRE |  |  | HVAC Control - Economizer
BLD16PRE |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD16PRE |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD16PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 5.14 | 9.07 | 7.71 | 12.22 | 4.7 | 9.03 | 5.67 | 13.72 | 13.59 | 9.35 | 19.19 | 18.75 | 22.24 | 23.83 | 24.18 | 32.89
BLD16PRE |  |  | BULKSTORAGE UNIT HEATERFAN | 0.8 | 2.54 | 0.8 | 4.09 | 0.8 | 2.4 | 0.82 | 4.99 | 4.62 | 2.68 | 7.8 | 7.25 | 9.38 | 10.04 | 10.36 | 15.04
BLD16PRE |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | 1.17 | 1.46 | 1.61 | 1.72 | 1.05 | 1.53 | 1.19 | 1.74 | 1.87 | 1.43 | 2.1 | 2.18 | 2.31 | 2.49 | 2.43 | 2.96
BLD16PRE |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | 3.17 | 5.07 | 5.3 | 6.41 | 2.85 | 5.1 | 3.66 | 6.99 | 7.1 | 5.24 | 9.29 | 9.32 | 10.55 | 11.3 | 11.39 | 14.89
BLD16PRE |  | Utility Costs
BLD16PRE |  |  | Electric Utility Rates
BLD16PRE |  |  | Average Annual Rate ($/kWh) | 0.087054 | 0.12197 | 0.11096 | 0.10419 | 0.13311 | 0.10154 | 0.14959 | 0.078736 | 0.037738 | 0.072453 | 0.053014 | 0.037692 | 0.06261 | 0.077933 | 0.060786 | 0.10003
BLD16PRE |  |  | Total Cost ($/m2) | 3.63 | 5.79 | 5.97 | 4.97 | 5.01 | 5.2 | 6.18 | 3.87 | 1.85 | 3.2 | 2.77 | 1.96 | 3.31 | 4.17 | 3.32 | 6.11
BLD16PRE |  |  | Gas Utility Rates
BLD16PRE |  |  | Average Annual Rate ($/MJ) | 0.011403 | 0.0080456 | 0.0080763 | 0.0094639 | 0.0087791 | 0.0075985 | 0.0086542 | 0.0096475 | 0.0068385 | 0.0084571 | 0.0082569 | 0.0068581 | 0.0079169 | 0.0079687 | 0.0078875 | 0.0041044
BLD16PRE |  |  | Total Cost ($/m2) | 0.12 | 0.91 | 0.64 | 2.1 | 0.6 | 1.08 | 1.29 | 3.66 | 1.93 | 2.28 | 4.41 | 2.84 | 6.03 | 4.72 | 7.45 | 6.83
BLD16PRE |  |  | Total Utility Costs
BLD16PRE |  |  | Cost Intensity ($/m2) | 3.75 | 6.7 | 6.61 | 7.07 | 5.61 | 6.27 | 7.46 | 7.52 | 3.78 | 5.49 | 7.18 | 4.8 | 9.34 | 8.89 | 10.77 | 12.94
BLD16PRE |  | Energy - End Uses
BLD16PRE |  |  | Electricity (kWh)
BLD16PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Cooling | 19680.5556 | 22222.2222 | 47672.2222 | 10891.6667 | 783.3333 | 35166.6667 | 433.3333 | 9358.3333 | 8297.2222 | 486.1111 | 5497.2222 | 4838.8889 | 3663.8889 | 2077.7778 | 1147.2222 | 113.8889
BLD16PRE |  |  | Interior Lighting | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111
BLD16PRE |  |  | Exterior Lighting | 47897.2222 | 47877.7778 | 47869.4444 | 47863.8889 | 47825 | 47813.8889 | 47841.6667 | 47811.1111 | 47830.5556 | 47736.1111 | 47819.4444 | 47791.6667 | 47788.8889 | 47777.7778 | 47750 | 47458.3333
BLD16PRE |  |  | Interior Equipment | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556
BLD16PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Fans | 16633.3333 | 41936.1111 | 47183.3333 | 54197.2222 | 15986.1111 | 46900 | 33902.7778 | 62700 | 63863.8889 | 48077.7778 | 81436.1111 | 81752.7778 | 86791.6667 | 91361.1111 | 97372.2222 | 130083.3333
BLD16PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total End Uses | 201777.7778 | 229605.5556 | 260291.6667 | 230516.6667 | 182161.1111 | 247450 | 199741.6667 | 237433.3333 | 237558.3333 | 213866.6667 | 252319.4444 | 251950 | 255811.1111 | 258783.3333 | 263833.3333 | 295222.2222
BLD16PRE |  |  | Gas (MJ)
BLD16PRE |  |  | Heating | 49380 | 544500 | 381420 | 1072030 | 329020 | 685660 | 717970 | 1832410 | 1362090 | 1305340 | 2581860 | 2000690 | 3683010 | 2861730 | 4569090 | 8044240
BLD16PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total End Uses | 49380 | 544500 | 381420 | 1072030 | 329020 | 685660 | 717970 | 1832410 | 1362090 | 1305340 | 2581860 | 2000690 | 3683010 | 2861730 | 4569090 | 8044240
BLD16PRE |  |  | Purchased Cooling (MJ)
BLD16PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Purchased Heating (MJ)
BLD16PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total Building (MJ) | 775780 | 1371080 | 1318470 | 1901890 | 984810 | 1576480 | 1437040 | 2687170 | 2217300 | 2075250 | 3490220 | 2907710 | 4603920 | 3793350 | 5518890 | 9107040
BLD16PRE |  | Energy - End Use Intensities
BLD16PRE |  |  | Electricity (MJ/m2)
BLD16PRE |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Cooling (elec) | 14.6532 | 16.5456 | 35.4944 | 8.1094 | 0.58323 | 26.1834 | 0.32264 | 6.9678 | 6.1777 | 0.36193 | 4.093 | 3.6028 | 2.728 | 1.547 | 0.85417 | 0.084796
BLD16PRE |  |  | Interior Lighting (elec) | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382
BLD16PRE |  |  | Exterior Lighting (elec) | 35.6619 | 35.6474 | 35.6412 | 35.6371 | 35.6081 | 35.5999 | 35.6206 | 35.5978 | 35.6123 | 35.542 | 35.604 | 35.5833 | 35.5813 | 35.573 | 35.5523 | 35.3351
BLD16PRE |  |  | Interior Equipment (elec) | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961
BLD16PRE |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Fans (elec) | 12.3844 | 31.2236 | 35.1304 | 40.3526 | 11.9025 | 34.9194 | 25.2423 | 46.6833 | 47.5499 | 35.7963 | 60.6333 | 60.8691 | 64.6208 | 68.023 | 72.4986 | 96.8537
BLD16PRE |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total End Uses | 150.2338 | 170.953 | 193.8004 | 171.6314 | 135.6282 | 184.2391 | 148.7178 | 176.7812 | 176.8743 | 159.2346 | 187.8646 | 187.5896 | 190.4644 | 192.6773 | 196.4373 | 219.8079
BLD16PRE |  |  | Gas (MJ/m2)
BLD16PRE |  |  | Heating (gas) | 10.2128 | 112.6133 | 78.8852 | 221.7169 | 68.0478 | 141.808 | 148.4903 | 378.9784 | 281.707 | 269.97 | 533.9794 | 413.782 | 761.7189 | 591.8621 | 944.9777 | 1663.7071
BLD16PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total End Uses | 10.2128 | 112.6133 | 78.8852 | 221.7169 | 68.0478 | 141.808 | 148.4903 | 378.9784 | 281.707 | 269.97 | 533.9794 | 413.782 | 761.7189 | 591.8621 | 944.9777 | 1663.7071
BLD16PRE |  |  | Purchased Cooling (MJ/m2)
BLD16PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Purchased Heating (MJ/m2)
BLD16PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total Building (MJ/m2) | 160.4466 | 283.5663 | 272.6855 | 393.3483 | 203.6781 | 326.0471 | 297.2081 | 555.7596 | 458.5813 | 429.2025 | 721.8462 | 601.3716 | 952.1812 | 784.5394 | 1141.415 | 1883.515
BLD16PRE |  | Peak Energy Demand
BLD16PRE |  |  | Electricity Peak Demand (kW)
BLD16PRE |  |  | Jan | 44.0366 | 49.7582 | 49.7915 | 52.2526 | 53.2978 | 60.2407 | 57.3376 | 64.4005 | 53.7538 | 60.558 | 69.098 | 69.1956 | 70.1791 | 71.7216 | 71.8382 | 78.6181
BLD16PRE |  |  | Feb | 44.4626 | 50.452 | 50.6311 | 52.2526 | 42.3398 | 49.2827 | 46.3796 | 53.4425 | 53.7538 | 49.6 | 69.098 | 58.2376 | 59.2211 | 60.7636 | 60.8802 | 78.6181
BLD16PRE |  |  | Mar | 45.0924 | 49.859 | 57.1316 | 52.3119 | 42.3679 | 49.6108 | 46.3796 | 53.4425 | 53.7538 | 49.6 | 58.14 | 58.2376 | 59.2211 | 60.7636 | 60.8802 | 71.1942
BLD16PRE |  |  | Apr | 48.9801 | 51.3729 | 61.7029 | 53.7895 | 43.1801 | 61.3622 | 46.3796 | 53.4789 | 54.5582 | 49.4253 | 57.4898 | 58.2376 | 59.2211 | 60.7636 | 60.8802 | 67.6601
BLD16PRE |  |  | May | 65.511 | 75.3642 | 82.7734 | 66.23 | 42.9807 | 77.9361 | 47.1939 | 55.8539 | 65.4079 | 50.3031 | 64.7055 | 65.1386 | 61.1183 | 60.9206 | 60.7379 | 66.338
BLD16PRE |  |  | Jun | 72.96 | 82.3739 | 110.0547 | 81.2429 | 43.7687 | 99.049 | 47.7798 | 84.9365 | 80.6403 | 53.0922 | 87.3049 | 79.0519 | 84.9147 | 83.4411 | 68.7304 | 71.8282
BLD16PRE |  |  | Jul | 72.0442 | 90.778 | 109.3314 | 97.6262 | 49.0935 | 98.1096 | 58.7102 | 95.5898 | 87.9215 | 63.8821 | 93.6473 | 88.2857 | 85.4182 | 84.7276 | 82.2027 | 75.6348
BLD16PRE |  |  | Aug | 74.1855 | 93.5159 | 110.0632 | 88.1803 | 55.6992 | 97.4618 | 54.0328 | 95.5455 | 88.0346 | 60.6601 | 91.3503 | 91.4062 | 86.1794 | 82.2658 | 79.249 | 76.3452
BLD16PRE |  |  | Sep | 70.491 | 82.6747 | 99.1625 | 74.8371 | 54.8912 | 95.4767 | 66.6313 | 75.6055 | 66.7372 | 58.7185 | 74.9776 | 75.1434 | 71.0862 | 69.3882 | 62.4136 | 66.338
BLD16PRE |  |  | Oct | 59.7616 | 64.5602 | 67.9732 | 58.5282 | 44.4113 | 64.8793 | 47.412 | 55.5632 | 55.2402 | 49.4253 | 58.7513 | 60.6439 | 58.8108 | 63.4393 | 59.9927 | 78.6181
BLD16PRE |  |  | Nov | 45.811 | 51.2246 | 53.924 | 51.9473 | 53.2978 | 60.2407 | 57.3376 | 64.0116 | 64.3575 | 60.3833 | 68.4478 | 69.1956 | 70.1791 | 71.7216 | 71.8382 | 78.6181
BLD16PRE |  |  | Dec | 44.3469 | 50.2479 | 49.7427 | 52.2526 | 53.2978 | 60.2407 | 57.3376 | 64.4005 | 64.7118 | 60.558 | 69.098 | 69.1956 | 70.1791 | 71.7216 | 71.8382 | 78.6181
BLD16PRE |  |  | Time of Peak Electrical Demand
BLD16PRE |  |  | Jan | 23-JAN-15:30 | 03-JAN-14:30 | 26-JAN-15:00 | 02-JAN-09:09 | 02-JAN-16:00 | 02-JAN-16:40 | 02-JAN-16:00 | 10-JAN-16:00 | 02-JAN-09:09 | 02-JAN-16:40 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
BLD16PRE |  |  | Feb | 22-FEB-15:00 | 21-FEB-14:00 | 28-FEB-15:00 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-16:00 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09
BLD16PRE |  |  | Mar | 13-MAR-15:00 | 27-MAR-14:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:39 | 31-MAR-14:00 | 01-MAR-09:09 | 01-MAR-09:09 | 13-MAR-08:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-08:09
BLD16PRE |  |  | Apr | 03-APR-14:00 | 21-APR-14:00 | 26-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:30 | 03-APR-08:09 | 05-APR-15:00 | 21-APR-15:00 | 03-APR-08:09 | 03-APR-08:09 | 04-APR-08:09 | 04-APR-08:09 | 04-APR-08:09 | 03-APR-08:09 | 03-APR-08:09
BLD16PRE |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-10:00 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 05-MAY-13:00 | 23-MAY-15:00 | 15-MAY-15:00 | 16-MAY-15:00 | 31-MAY-15:00 | 01-MAY-08:09
BLD16PRE |  |  | Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-15:00 | 29-JUN-15:20 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 30-JUN-14:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
BLD16PRE |  |  | Jul | 10-JUL-13:50 | 31-JUL-13:00 | 11-JUL-15:00 | 03-JUL-15:30 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:50 | 13-JUL-14:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
BLD16PRE |  |  | Aug | 21-AUG-14:50 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-15:20 | 15-AUG-12:09 | 17-AUG-14:00 | 01-AUG-14:09 | 07-AUG-15:30 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-15:00
BLD16PRE |  |  | Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-15:00 | 11-SEP-13:00 | 25-SEP-12:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 01-SEP-14:00 | 01-SEP-15:00 | 05-SEP-13:00 | 06-SEP-15:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 01-SEP-08:09
BLD16PRE |  |  | Oct | 06-OCT-14:30 | 06-OCT-15:00 | 02-OCT-15:50 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:20 | 30-OCT-13:50 | 03-OCT-14:09 | 13-OCT-14:00 | 02-OCT-08:09 | 31-OCT-13:39 | 05-OCT-15:00 | 06-OCT-14:00 | 30-OCT-07:10 | 02-OCT-08:09 | 23-OCT-08:09
BLD16PRE |  |  | Nov | 07-NOV-14:00 | 03-NOV-14:30 | 13-NOV-15:00 | 01-NOV-08:09 | 06-NOV-16:00 | 06-NOV-16:40 | 10-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 06-NOV-16:49 | 06-NOV-16:40 | 17-NOV-16:40 | 13-NOV-16:49 | 29-NOV-16:40 | 10-NOV-16:40 | 01-NOV-08:09
BLD16PRE |  |  | Dec | 19-DEC-14:30 | 19-DEC-15:30 | 01-DEC-09:09 | 07-DEC-09:09 | 01-DEC-16:49 | 01-DEC-16:30 | 01-DEC-16:49 | 14-DEC-16:40 | 21-DEC-16:00 | 11-DEC-16:40 | 05-DEC-16:19 | 01-DEC-16:40 | 04-DEC-16:30 | 04-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
BLD16PRE |  | Source Energy
BLD16PRE |  |  | Total Source Energy (GJ) | 2463.39 | 3596.73 | 3380.41 | 3962.31 | 2388.95 | 3935.19 | 3009.55 | 5057.62 | 4324.98 | 2766.62 | 6040.42 | 5194.26 | 7187.03 | 6363.33 | 8253.91 | 12580.62
BLD16PRE |  |  | Total Source Energy (MJ/m2) | 509.48 | 743.87 | 699.14 | 819.48 | 494.08 | 813.88 | 622.44 | 1046.02 | 894.49 | 572.19 | 1249.28 | 1074.28 | 1486.42 | 1316.06 | 1707.07 | 2601.92
BLD16PRE |  | Water Consumption (m3)
BLD16PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  | Emissions
BLD16PRE |  |  | Carbon Equivalent (kg) | 56228.0116 | 86406.0734 | 85454.0759 | 90339.4145 | 27221.7229 | 95822.7307 | 36290.0332 | 97116.2498 | 121604.1271 | 39115.4473 | 181082.5028 | 138999.4077 | 153976.5455 | 146174.229 | 172701.5099 | 228130.9782
BLD16PRE |  |  | CO2 (kg) | 130709.7638 | 220547.8352 | 204659.1223 | 217012.0853 | 73978.9249 | 233395.1587 | 99728.3437 | 239154.233 | 297082.0281 | 105010.1372 | 444899.575 | 344053.1152 | 393749.362 | 369052.3876 | 446245.9936 | 627200.4144
BLD16PRE |  |  | NOX (kg) | 228.319 | 278.3571 | 330.3614 | 361.9054 | 64.2023 | 356.6 | 87.2937 | 373.959 | 461.1582 | 121.1953 | 687.3 | 515.4011 | 542.5725 | 525.8032 | 596.0385 | 641.1964
BLD16PRE |  |  | SO2 (kg) | 863.7043 | 1095.3618 | 1046.7919 | 809.403 | 530.1585 | 1361.3524 | 581.4187 | 867.2216 | 1037.7334 | 165.6508 | 1701.1308 | 1100.7564 | 604.7394 | 691.7522 | 623.9144 | 1504.9489
BLD16PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PRE |  |  | Hg (kg) | 0.0039 | 0.0031 | 0.0029 | 0.0031 | 0.0003 | 0.0026 | 0.0003 | 0.0037 | 0.0042 | 0.0008 | 0.0054 | 0.0045 | 0.0048 | 0.0051 | 0.005 | 0.006
BLD16PRE |  |  | Water for Electricity (m3) | 106.8936 | 373.5942 | 7731.84 | 1439.26 | 3198.36 | 6788.52 | 3507.03 | 53.9065 | 1078.7 | 2185.02 | 391.4603 | 1144.06 | 396.8738 | 16392.5 | 409.3223 | 301.6214
BLD16PST |  | Program
BLD16PST |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD16PST |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD16PST |  |  | Weighting Factor
BLD16PST |  | Fabric
BLD16PST |  |  | Exterior walls
BLD16PST | TypeWall |  | Construction Type | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall
BLD16PST | RvalWall |  | R-value (m2·K / W) | 0.2291 | 0.98232 | 0.5423 | 1.1628 | 0.60901 | 0.90909 | 1.1628 | 1.7889 | 1.5699 | 1.7241 | 1.9569 | 1.9569 | 2.5189 | 2.2523 | 2.849 | 3.7175
BLD16PST |  |  | Roof
BLD16PST | TypeRoof |  | Construction Type | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof
BLD16PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD16PST |  |  | Window
BLD16PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD16PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.702
BLD16PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.633
BLD16PST |  |  | Skylights/TDD
BLD16PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD16PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD16PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD16PST |  |  | Foundation
BLD16PST |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD16PST |  |  | Construction | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade
BLD16PST |  |  | R-value (m2·K / W) | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809
BLD16PST |  | HVAC
BLD16PST |  |  | HVAC Sizing
BLD16PST | HVAC |  | Air Conditioning (kW) | 109.4302 | 146.4754 | 129.9179 | 178.3724 | 90.3996 | 128.2802 | 85.0889 | 193.622 | 170.1054 | 120.8683 | 257.905 | 232.5398 | 289.3057 | 243.6532 | 306.7005 | 269.6977
BLD16PST |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 28.6981 | 30.7526 | 28.9916 | 32.7141 | 19.3824 | 23.3193 | 17.5273 | 34.4084 | 26.9041 | 20.843 | 42.3393 | 31.4575 | 44.7789 | 36.2358 | 44.2149 | 42.766
BLD16PST |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 80.7321 | 115.7228 | 100.9263 | 145.6583 | 71.0172 | 104.9609 | 67.5616 | 159.2135 | 143.2013 | 100.0253 | 215.5656 | 201.0823 | 244.5268 | 207.4173 | 262.4856 | 226.9317
BLD16PST | HEAT |  | Heating (kW) | 150.4944 | 272.1712 | 168.8369 | 361.9632 | 151.7525 | 242.2456 | 168.3537 | 428.3134 | 340.8525 | 284.0629 | 615.8139 | 486.2921 | 712.1072 | 684.0542 | 754.9443 | 1066.1421
BLD16PST |  |  | BULKSTORAGE UNIT HEATER COIL | 39.3476 | 95.9475 | 35.0601 | 151.0271 | 39.2079 | 79.6208 | 36.1869 | 192.2765 | 143.1293 | 104.0834 | 305.5756 | 229.4699 | 364.8319 | 350.3473 | 390.8667 | 580.9633
BLD16PST |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 27.9592 | 31.5248 | 28.1379 | 34.6891 | 24.626 | 30.3605 | 25.4186 | 36.4615 | 32.252 | 30.0788 | 44.4436 | 37.8745 | 47.8505 | 46.2252 | 49.3977 | 62.3072
BLD16PST |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 83.1876 | 144.6988 | 105.6388 | 176.247 | 87.9187 | 132.2643 | 106.7481 | 199.5754 | 165.4712 | 149.9008 | 265.7947 | 218.9477 | 299.4249 | 287.4817 | 314.68 | 422.8715
BLD16PST |  |  | HVAC Efficiency
BLD16PST | COP |  | Air Conditioning (COP) | 3.3008 | 3.2867 | 3.2903 | 3.2795 | 3.2879 | 3.2791 | 3.3762 | 3.278 | 3.2727 | 3.2766 | 3.2415 | 3.2665 | 3.1563 | 3.2702 | 3.1545 | 3.157
BLD16PST |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3
BLD16PST |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.13 | 3.23 | 3.13 | 3.13
BLD16PST | EffHeat |  | Heating Efficiency (%) | 0.78372 | 0.78232 | 0.78333 | 0.78192 | 0.78325 | 0.78251 | 0.78302 | 0.7817 | 0.78189 | 0.78212 | 0.78144 | 0.78156 | 0.78134 | 0.78135 | 0.78131 | 0.78117
BLD16PST |  |  | BULKSTORAGE UNIT HEATER COIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD16PST |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD16PST |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD16PST |  |  | HVAC Control - Economizer
BLD16PST |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD16PST |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD16PST | Fan |  | Fan Max Flow Rate (m3/s ) | 5.31 | 8.13 | 6.38 | 10.9 | 4.7 | 7.89 | 5.3 | 12.27 | 12.01 | 8.46 | 17.63 | 16.75 | 20.39 | 21.98 | 22.03 | 29.73
BLD16PST |  |  | BULKSTORAGE UNIT HEATERFAN | 0.8 | 2.16 | 0.8 | 3.54 | 0.8 | 1.92 | 0.8 | 4.35 | 3.92 | 2.34 | 7.08 | 6.31 | 8.52 | 9.18 | 9.33 | 13.44
BLD16PST |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | 1.26 | 1.31 | 1.52 | 1.49 | 1.04 | 1.37 | 1.06 | 1.51 | 1.63 | 1.26 | 1.87 | 1.9 | 2.02 | 2.19 | 2.13 | 2.58
BLD16PST |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | 3.25 | 4.66 | 4.06 | 5.87 | 2.86 | 4.6 | 3.44 | 6.41 | 6.46 | 4.86 | 8.68 | 8.54 | 9.85 | 10.61 | 10.57 | 13.71
BLD16PST |  | Utility Costs
BLD16PST |  |  | Electric Utility Rates
BLD16PST |  |  | Average Annual Rate ($/kWh) | 0.087563 | 0.12078 | 0.10982 | 0.10459 | 0.13324 | 0.10142 | 0.14985 | 0.078219 | 0.037769 | 0.072458 | 0.053122 | 0.03772 | 0.062358 | 0.077628 | 0.060539 | 0.099933
BLD16PST |  |  | Total Cost ($/m2) | 3.71 | 5.55 | 5.51 | 4.83 | 5.02 | 4.94 | 5.76 | 3.71 | 1.79 | 3.15 | 2.7 | 1.9 | 3.21 | 4.04 | 3.2 | 5.87
BLD16PST |  |  | Gas Utility Rates
BLD16PST |  |  | Average Annual Rate ($/MJ) | 0.011402 | 0.008044 | 0.0080721 | 0.0094672 | 0.0087766 | 0.0075958 | 0.0086603 | 0.0096475 | 0.0068384 | 0.0084595 | 0.0082556 | 0.006856 | 0.0079196 | 0.0079654 | 0.0078894 | 0.0041049
BLD16PST |  |  | Total Cost ($/m2) | 0.13 | 0.82 | 0.61 | 1.88 | 0.6 | 0.95 | 1.24 | 3.25 | 1.69 | 2.06 | 4.01 | 2.51 | 5.5 | 4.3 | 6.75 | 6.11
BLD16PST |  |  | Total Utility Costs
BLD16PST |  |  | Cost Intensity ($/m2) | 3.83 | 6.37 | 6.13 | 6.7 | 5.62 | 5.9 | 7 | 6.97 | 3.48 | 5.21 | 6.7 | 4.41 | 8.71 | 8.34 | 9.95 | 11.98
BLD16PST |  | Energy - End Uses
BLD16PST |  |  | Electricity (kWh)
BLD16PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Cooling | 21788.8889 | 18333.3333 | 39580.5556 | 8597.2222 | 794.4444 | 28319.4444 | 405.5556 | 7400 | 6075 | 352.7778 | 4508.3333 | 3672.2222 | 3016.6667 | 1619.4444 | 919.4444 | 97.2222
BLD16PST |  |  | Interior Lighting | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111 | 88561.1111
BLD16PST |  |  | Exterior Lighting | 47897.2222 | 47877.7778 | 47869.4444 | 47863.8889 | 47825 | 47813.8889 | 47841.6667 | 47811.1111 | 47830.5556 | 47736.1111 | 47819.4444 | 47791.6667 | 47788.8889 | 47777.7778 | 47750 | 47458.3333
BLD16PST |  |  | Interior Equipment | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556
BLD16PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Fans | 17333.3333 | 38488.8889 | 37647.2222 | 49086.1111 | 16025 | 41933.3333 | 20013.8889 | 56866.6667 | 57436.1111 | 44386.1111 | 75450 | 74155.5556 | 80327.7778 | 84850 | 89636.1111 | 119019.4444
BLD16PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total End Uses | 204588.8889 | 222266.6667 | 242666.6667 | 223113.8889 | 182213.8889 | 235636.1111 | 185827.7778 | 229644.4444 | 228905.5556 | 210041.6667 | 245347.2222 | 243188.8889 | 248700 | 251816.6667 | 255872.2222 | 284141.6667
BLD16PST |  |  | Gas (MJ)
BLD16PST |  |  | Heating | 53210 | 492860 | 367920 | 959100 | 330720 | 606930 | 691680 | 1630630 | 1195710 | 1178820 | 2347680 | 1768930 | 3360460 | 2611410 | 4133880 | 7194410
BLD16PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total End Uses | 53210 | 492860 | 367920 | 959100 | 330720 | 606930 | 691680 | 1630630 | 1195710 | 1178820 | 2347680 | 1768930 | 3360460 | 2611410 | 4133880 | 7194410
BLD16PST |  |  | Purchased Cooling (MJ)
BLD16PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Purchased Heating (MJ)
BLD16PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total Building (MJ) | 789730 | 1293020 | 1241520 | 1762310 | 986690 | 1455220 | 1360660 | 2457360 | 2019770 | 1934970 | 3230930 | 2644410 | 4255780 | 3517940 | 5055030 | 8217320
BLD16PST |  | Energy - End Use Intensities
BLD16PST |  |  | Electricity (MJ/m2)
BLD16PST |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Cooling (elec) | 16.2229 | 13.6501 | 29.4697 | 6.4011 | 0.5915 | 21.0853 | 0.30196 | 5.5097 | 4.5231 | 0.26266 | 3.3567 | 2.7342 | 2.2461 | 1.2058 | 0.68457 | 0.072387
BLD16PST |  |  | Interior Lighting (elec) | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382 | 65.9382
BLD16PST |  |  | Exterior Lighting (elec) | 35.6619 | 35.6474 | 35.6412 | 35.6371 | 35.6081 | 35.5999 | 35.6206 | 35.5978 | 35.6123 | 35.542 | 35.604 | 35.5833 | 35.5813 | 35.573 | 35.5523 | 35.3351
BLD16PST |  |  | Interior Equipment (elec) | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961
BLD16PST |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Fans (elec) | 12.9055 | 28.6569 | 28.0303 | 36.5471 | 11.9314 | 31.2215 | 14.9014 | 42.3401 | 42.7641 | 33.0477 | 56.1764 | 55.2126 | 59.8081 | 63.1751 | 66.7386 | 88.616
BLD16PST |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total End Uses | 152.3268 | 165.4888 | 180.6777 | 166.1196 | 135.6675 | 175.4431 | 138.3582 | 170.982 | 170.4318 | 156.3867 | 182.6735 | 181.0665 | 185.1698 | 187.4903 | 190.5099 | 211.5579
BLD16PST |  |  | Gas (MJ/m2)
BLD16PST |  |  | Heating (gas) | 11.0049 | 101.9331 | 76.0931 | 198.3607 | 68.3994 | 125.5251 | 143.053 | 337.2464 | 247.2963 | 243.8032 | 485.5464 | 365.8495 | 695.0092 | 540.091 | 854.9677 | 1487.9455
BLD16PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total End Uses | 11.0049 | 101.9331 | 76.0931 | 198.3607 | 68.3994 | 125.5251 | 143.053 | 337.2464 | 247.2963 | 243.8032 | 485.5464 | 365.8495 | 695.0092 | 540.091 | 854.9677 | 1487.9455
BLD16PST |  |  | Purchased Cooling (MJ/m2)
BLD16PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Purchased Heating (MJ/m2)
BLD16PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total Building (MJ/m2) | 163.3317 | 267.422 | 256.7708 | 364.4804 | 204.0669 | 300.9681 | 281.4113 | 508.2304 | 417.7282 | 400.1899 | 668.2199 | 546.916 | 880.179 | 727.5792 | 1045.4796 | 1699.5034
BLD16PST |  | Peak Energy Demand
BLD16PST |  |  | Electricity Peak Demand (kW)
BLD16PST |  |  | Jan | 44.7733 | 48.3991 | 47.3233 | 50.9221 | 53.3009 | 59.1807 | 53.9595 | 63 | 52.2172 | 59.6876 | 67.653 | 67.353 | 68.6004 | 70.1328 | 70.0193 | 76.0678
BLD16PST |  |  | Feb | 45.3334 | 48.7265 | 47.6994 | 50.9221 | 42.3429 | 48.2227 | 43.0015 | 52.042 | 52.2172 | 48.7296 | 67.653 | 56.395 | 57.6424 | 59.1748 | 59.0613 | 76.0678
BLD16PST |  |  | Mar | 45.986 | 48.3195 | 49.6417 | 50.9221 | 42.3429 | 48.2227 | 43.0015 | 52.042 | 52.2172 | 48.7296 | 56.695 | 56.395 | 57.6424 | 59.1748 | 59.0613 | 68.644
BLD16PST |  |  | Apr | 52.0319 | 49.9461 | 52.4666 | 51.7423 | 43.0747 | 53.0246 | 43.0015 | 51.7121 | 52.3945 | 48.5871 | 56.1123 | 56.395 | 56.9256 | 59.1748 | 59.0613 | 65.1098
BLD16PST |  |  | May | 68.2977 | 69.7949 | 73.8375 | 61.0965 | 42.9133 | 69.7122 | 43.3839 | 53.4175 | 59.7095 | 48.9701 | 59.7592 | 59.3816 | 58.9153 | 59.0236 | 58.7584 | 63.9365
BLD16PST |  |  | Jun | 74.6684 | 76.1349 | 95.7427 | 75.0724 | 43.7339 | 94.5156 | 44.1091 | 78.87 | 73.9055 | 50.0975 | 81.5885 | 73.0968 | 80.2147 | 78.1227 | 63.2402 | 65.9762
BLD16PST |  |  | Jul | 73.5351 | 83.5967 | 95.2651 | 90.3326 | 49.6378 | 93.7451 | 53.3272 | 88.7463 | 80.1904 | 60.7117 | 87.7949 | 81.7694 | 81.645 | 79.7827 | 77.266 | 70.6823
BLD16PST |  |  | Aug | 75.5409 | 87.0318 | 95.7469 | 81.7062 | 56.3776 | 93.2048 | 48.5814 | 88.501 | 80.8428 | 58.0891 | 85.9121 | 84.6476 | 81.643 | 78.0352 | 74.834 | 71.7647
BLD16PST |  |  | Sep | 73.0588 | 77.3544 | 89.0546 | 69.2397 | 55.3027 | 89.4645 | 59.5228 | 69.7023 | 62.2308 | 55.9079 | 70.6098 | 70.0348 | 67.3801 | 64.9791 | 60.4529 | 63.9365
BLD16PST |  |  | Oct | 62.4125 | 59.9696 | 60.2955 | 53.2053 | 44.333 | 58.0305 | 43.6151 | 53.5643 | 53.1822 | 48.5871 | 57.0951 | 57.55 | 56.9568 | 61.9305 | 58.2697 | 76.0678
BLD16PST |  |  | Nov | 47.4275 | 49.7963 | 49.6412 | 50.6679 | 53.3009 | 59.1807 | 53.9595 | 62.6701 | 62.8852 | 59.5451 | 67.0703 | 66.8417 | 68.6004 | 70.1328 | 70.0193 | 76.0678
BLD16PST |  |  | Dec | 45.0962 | 48.4585 | 47.3233 | 50.9221 | 53.3009 | 59.1807 | 53.9595 | 63 | 63.1752 | 59.6876 | 67.653 | 67.353 | 68.6004 | 70.1328 | 70.0193 | 76.0678
BLD16PST |  |  | Time of Peak Electrical Demand
BLD16PST |  |  | Jan | 06-JAN-13:00 | 11-JAN-09:09 | 02-JAN-09:09 | 02-JAN-09:09 | 02-JAN-16:00 | 02-JAN-16:40 | 02-JAN-16:00 | 10-JAN-16:00 | 02-JAN-09:09 | 02-JAN-16:40 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
BLD16PST |  |  | Feb | 22-FEB-13:00 | 23-FEB-15:00 | 28-FEB-15:00 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-16:00 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09
BLD16PST |  |  | Mar | 13-MAR-15:39 | 27-MAR-14:00 | 17-MAR-14:00 | 13-MAR-08:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 13-MAR-08:09 | 02-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-08:09
BLD16PST |  |  | Apr | 03-APR-14:00 | 21-APR-14:00 | 26-APR-15:00 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:00 | 03-APR-08:09 | 03-APR-08:09 | 21-APR-15:00 | 03-APR-08:09 | 03-APR-08:09 | 04-APR-08:09 | 03-APR-08:09 | 04-APR-08:09 | 03-APR-08:09 | 03-APR-08:09
BLD16PST |  |  | May | 24-MAY-14:00 | 18-MAY-15:39 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-10:00 | 31-MAY-15:00 | 17-MAY-13:00 | 15-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 05-MAY-13:00 | 23-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 01-MAY-08:09
BLD16PST |  |  | Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-15:00 | 29-JUN-15:39 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 30-JUN-14:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
BLD16PST |  |  | Jul | 10-JUL-13:50 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:50 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 03-JUL-14:00 | 17-JUL-15:50 | 13-JUL-14:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
BLD16PST |  |  | Aug | 21-AUG-14:50 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-15:20 | 15-AUG-12:20 | 17-AUG-15:30 | 01-AUG-13:00 | 07-AUG-15:30 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-15:00
BLD16PST |  |  | Sep | 11-SEP-14:00 | 15-SEP-14:00 | 08-SEP-15:00 | 11-SEP-13:00 | 25-SEP-12:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 14-SEP-15:00 | 01-SEP-15:00 | 27-SEP-15:00 | 06-SEP-15:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 01-SEP-08:09
BLD16PST |  |  | Oct | 06-OCT-14:20 | 06-OCT-15:00 | 02-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 04-OCT-14:00 | 30-OCT-14:30 | 03-OCT-14:00 | 13-OCT-14:00 | 02-OCT-08:09 | 31-OCT-13:39 | 05-OCT-14:00 | 06-OCT-14:00 | 30-OCT-07:10 | 02-OCT-08:09 | 23-OCT-08:09
BLD16PST |  |  | Nov | 07-NOV-14:00 | 03-NOV-14:30 | 13-NOV-15:20 | 01-NOV-08:09 | 06-NOV-16:00 | 06-NOV-16:40 | 10-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 06-NOV-16:49 | 06-NOV-16:40 | 06-NOV-16:49 | 13-NOV-16:49 | 29-NOV-16:40 | 21-NOV-16:30 | 01-NOV-08:09
BLD16PST |  |  | Dec | 19-DEC-14:20 | 19-DEC-15:39 | 01-DEC-09:09 | 07-DEC-09:09 | 01-DEC-16:49 | 01-DEC-16:30 | 01-DEC-16:49 | 14-DEC-16:40 | 21-DEC-16:00 | 11-DEC-16:00 | 05-DEC-16:19 | 01-DEC-16:40 | 04-DEC-16:30 | 04-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
BLD16PST |  | Source Energy
BLD16PST |  |  | Total Source Energy (GJ) | 2501.13 | 3444.39 | 3164.96 | 3749.33 | 2391.37 | 3697.1 | 2825.8 | 4737.02 | 4039.95 | 2604.48 | 5695.66 | 4836.51 | 6746.84 | 6002.77 | 7680.17 | 11510.12
BLD16PST |  |  | Total Source Energy (MJ/m2) | 517.28 | 712.37 | 654.58 | 775.44 | 494.58 | 764.63 | 584.43 | 979.71 | 835.54 | 538.66 | 1177.97 | 1000.29 | 1395.38 | 1241.49 | 1588.41 | 2380.52
BLD16PST |  | Water Consumption (m3)
BLD16PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  | Emissions
BLD16PST |  |  | Carbon Equivalent (kg) | 57067.7496 | 83027.3209 | 79889.456 | 86022.224 | 27258.27 | 90418.687 | 34189.7188 | 91375.8402 | 115069.3994 | 36555.4792 | 173141.0719 | 131240.6798 | 145726.6233 | 139113.5743 | 162128.5871 | 209688.4917
BLD16PST |  |  | CO2 (kg) | 132693.8696 | 211715.7704 | 191441.9538 | 205952.0693 | 74083.2014 | 219856.3796 | 94016.8614 | 223928.2509 | 280178.0897 | 97757.01 | 424119.1338 | 323637.8825 | 371334.4567 | 350087.3941 | 417289.6303 | 575114.2251
BLD16PST |  |  | NOX (kg) | 231.6473 | 267.842 | 308.5725 | 346.5681 | 64.2961 | 337.4003 | 82.3346 | 354.9909 | 438.8386 | 114.1479 | 660.6006 | 489.8052 | 517.0783 | 503.4487 | 563.9894 | 591.2151
BLD16PST |  |  | SO2 (kg) | 875.7329 | 1060.3487 | 975.9067 | 783.3834 | 530.3082 | 1296.3493 | 540.9197 | 838.7355 | 999.9049 | 162.6605 | 1654.0646 | 1062.4309 | 587.8732 | 673.0775 | 605.0085 | 1448.3221
BLD16PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16PST |  |  | Hg (kg) | 0.004 | 0.003 | 0.0027 | 0.003 | 0.0003 | 0.0025 | 0.0003 | 0.0036 | 0.004 | 0.0008 | 0.0052 | 0.0043 | 0.0047 | 0.0049 | 0.0049 | 0.0057
BLD16PST |  |  | Water for Electricity (m3) | 108.3822 | 361.6555 | 7208.24 | 1393.03 | 3199.26 | 6464.44 | 3262.71 | 52.1382 | 1039.41 | 2145.94 | 380.6396 | 1104.27 | 385.8437 | 15951 | 396.9713 | 290.3017
BLD16NEW |  | Program
BLD16NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD16NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD16NEW |  |  | Weighting Factor | 88.7974 | 658.6289 | 147.5727 | 754.1966 |  | 584.3224 | 39.0954 | 621.8326 | 17.2482 | 110.7246 | 910.1259 | 175.0078 | 118.4487 | 12.4546 | 10.9617 | 0.56144
BLD16NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD16NEW |  |  | Exterior walls
BLD16NEW | TypeWall |  | Construction Type | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall | MetalWall
BLD16NEW | RvalWall |  | R-value (m2·K / W) | 0.2291 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 0.7657 | 1.1223 | 1.1223 | 1.1223 | 1.2407 | 1.2407 | 1.3661 | 1.3661 | 1.3661 | 1.3661
BLD16NEW |  |  | Roof
BLD16NEW | TypeRoof |  | Construction Type | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof | MetalRoof
BLD16NEW | RvalRoof |  | R-value (m2·K / W) | 0.18847 | 1.0515 | 1.0515 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8116 | 1.8657 | 1.8657 | 1.8657 | 1.8657 | 1.8116 | 2.5
BLD16NEW |  |  | Window
BLD16NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835
BLD16NEW | SHGC |  | SHGC | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BLD16NEW |  |  | Visible transmittance | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603 | 0.603
BLD16NEW |  |  | Skylights/TDD
BLD16NEW |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD16NEW |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD16NEW |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD16NEW |  |  | Foundation
BLD16NEW |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD16NEW |  |  | Construction | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade | 8in slab-on-grade
BLD16NEW |  |  | R-value (m2·K / W) | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809 | 0.39809
BLD16NEW |  | HVAC
BLD16NEW |  |  | HVAC Sizing
BLD16NEW | HVAC |  | Air Conditioning (kW) | 357.2415 | 121.4741 | 130.6539 | 110.7776 | 57.0132 | 87.1247 | 57.1165 | 116.1541 | 97.9004 | 71.2217 | 149.1937 | 127.1999 | 166.502 | 135.5043 | 178.3224 | 150.1451
BLD16NEW |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 22.0861 | 19.2571 | 18.8806 | 21.0199 | 13.7603 | 17.0576 | 13.8889 | 20.6442 | 20.0677 | 16.0568 | 24.1654 | 22.6181 | 25.1705 | 24.8526 | 25.0987 | 27.8349
BLD16NEW |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 335.1554 | 102.217 | 111.7733 | 89.7577 | 43.2529 | 70.0671 | 43.2277 | 95.5099 | 77.8327 | 55.1649 | 125.0283 | 104.5818 | 141.3315 | 110.6517 | 153.2237 | 122.3102
BLD16NEW | HEAT |  | Heating (kW) | 172.0249 | 194.267 | 133.488 | 216.7679 | 114.7011 | 154.8652 | 127.7757 | 247.6128 | 209.5607 | 160.4572 | 345.8662 | 287.6877 | 401.336 | 395.5533 | 433.9112 | 565.6953
BLD16NEW |  |  | BULKSTORAGE UNIT HEATER COIL | 31.4781 | 65.0562 | 35.0601 | 76.7305 | 39.2079 | 41.9101 | 36.1869 | 96.9069 | 75.8177 | 44.1586 | 154.4995 | 120.0761 | 188.0875 | 186.0076 | 207.2885 | 285.0474
BLD16NEW |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 23.8184 | 23.9123 | 19.9695 | 26.7943 | 18.2755 | 23.1599 | 20.3598 | 26.5845 | 24.4226 | 22.2641 | 31.0449 | 27.765 | 33.1375 | 32.4732 | 34.5377 | 41.8321
BLD16NEW |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 116.7284 | 105.2984 | 78.4584 | 113.243 | 57.2177 | 89.7951 | 71.229 | 124.1214 | 109.3203 | 94.0345 | 160.3218 | 139.8467 | 180.111 | 177.0725 | 192.0849 | 238.8159
BLD16NEW |  |  | HVAC Efficiency
BLD16NEW | COP |  | Air Conditioning (COP) | 3.1529 | 3.2728 | 3.2936 | 3.2812 | 3.3893 | 3.3724 | 3.39 | 3.278 | 3.2853 | 3.3834 | 3.2737 | 3.278 | 3.2708 | 3.2795 | 3.268 | 3.2801
BLD16NEW |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
BLD16NEW |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.23 | 3.23 | 3.23 | 3.3 | 3.3 | 3.3 | 3.23 | 3.23 | 3.3 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD16NEW | EffHeat |  | Heating Efficiency (%) | 0.78277 | 0.78246 | 0.78299 | 0.78247 | 0.79316 | 0.78299 | 0.78319 | 0.78215 | 0.78233 | 0.78278 | 0.7818 | 0.78193 | 0.78165 | 0.78164 | 0.78159 | 0.78148
BLD16NEW |  |  | BULKSTORAGE UNIT HEATER COIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD16NEW |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD16NEW |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD16NEW |  |  | HVAC Control - Economizer
BLD16NEW |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD16NEW |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD16NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 19.57 | 6.6 | 7.08 | 6.41 | 3.6 | 5.37 | 3.88 | 6.9 | 7.25 | 4.74 | 9.54 | 9.65 | 11.05 | 12.28 | 12.19 | 15.05
BLD16NEW |  |  | BULKSTORAGE UNIT HEATERFAN | 0.8 | 1.39 | 0.8 | 1.62 | 0.8 | 0.91 | 0.8 | 1.97 | 1.89 | 0.83 | 3.24 | 3 | 4 | 4.48 | 4.53 | 5.98
BLD16NEW |  |  | FURNACE_PACU_CAV_1:1_UNITARY_PACKAGE_FAN | 1.2 | 0.98 | 1.08 | 1.14 | 0.83 | 1.03 | 0.84 | 1.08 | 1.21 | 0.97 | 1.27 | 1.37 | 1.36 | 1.5 | 1.45 | 1.68
BLD16NEW |  |  | FURNACE_PACU_CAV_2:2_UNITARY_PACKAGE_FAN | 17.57 | 4.23 | 5.2 | 3.65 | 1.97 | 3.43 | 2.24 | 3.85 | 4.15 | 2.94 | 5.03 | 5.28 | 5.69 | 6.3 | 6.21 | 7.39
BLD16NEW |  | Utility Costs
BLD16NEW |  |  | Electric Utility Rates
BLD16NEW |  |  | Average Annual Rate ($/kWh) | 0.097442 | 0.12068 | 0.10992 | 0.10307 | 0.13389 | 0.10192 | 0.1506 | 0.079436 | 0.037661 | 0.078372 | 0.052785 | 0.037641 | 0.063908 | 0.079676 | 0.062985 | 0.10379
BLD16NEW |  |  | Total Cost ($/m2) | 8.66 | 6.79 | 6.77 | 5.52 | 6.42 | 5.44 | 7.26 | 4.29 | 2.05 | 3.85 | 2.93 | 2.1 | 3.62 | 4.55 | 3.62 | 6.21
BLD16NEW |  |  | Gas Utility Rates
BLD16NEW |  |  | Average Annual Rate ($/MJ) | 0.01137 | 0.0080412 | 0.0080776 | 0.009471 | 0.0088194 | 0.0075965 | 0.0087051 | 0.0096359 | 0.0068419 | 0.0084743 | 0.0082569 | 0.0068526 | 0.007924 | 0.0079517 | 0.0079006 | 0.0041052
BLD16NEW |  |  | Total Cost ($/m2) | 0.13 | 0.5 | 0.41 | 1.01 | 0.37 | 0.62 | 0.74 | 1.61 | 0.89 | 1.2 | 1.87 | 1.26 | 2.52 | 2.07 | 3.13 | 2.74
BLD16NEW |  |  | Total Utility Costs
BLD16NEW |  |  | Cost Intensity ($/m2) | 8.79 | 7.29 | 7.18 | 6.54 | 6.79 | 6.06 | 8 | 5.9 | 2.94 | 5.05 | 4.8 | 3.37 | 6.14 | 6.62 | 6.75 | 8.96
BLD16NEW |  | Energy - End Uses
BLD16NEW |  |  | Electricity (kWh)
BLD16NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Cooling | 102244.4444 | 19052.7778 | 35319.4444 | 7794.4444 | 1044.4444 | 19277.7778 | 450 | 6647.2222 | 6019.4444 | 575 | 4344.4444 | 3827.7778 | 3363.8889 | 1941.6667 | 1305.5556 | 263.8889
BLD16NEW |  |  | Interior Lighting | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778 | 151402.7778
BLD16NEW |  |  | Exterior Lighting | 39002.7778 | 38988.8889 | 38980.5556 | 38975 | 38944.4444 | 38936.1111 | 38955.5556 | 38933.3333 | 38947.2222 | 38869.4444 | 38938.8889 | 38916.6667 | 38913.8889 | 38905.5556 | 38883.3333 | 38644.4444
BLD16NEW |  |  | Interior Equipment | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556 | 29005.5556
BLD16NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Fans | 108011.1111 | 33586.1111 | 42977.7778 | 31975 | 11394.4444 | 19655.5556 | 13430.5556 | 35127.7778 | 37397.2222 | 17786.1111 | 44647.2222 | 46883.3333 | 50986.1111 | 55033.3333 | 57036.1111 | 70169.4444
BLD16NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total End Uses | 429669.4444 | 272033.3333 | 297688.8889 | 259152.7778 | 231794.4444 | 258280.5556 | 233247.2222 | 261119.4444 | 262772.2222 | 237638.8889 | 268338.8889 | 270036.1111 | 273672.2222 | 276288.8889 | 277633.3333 | 289486.1111
BLD16NEW |  |  | Gas (MJ)
BLD16NEW |  |  | Heating | 56480 | 301980 | 244620 | 517240 | 205400 | 392460 | 408410 | 805640 | 629390 | 682230 | 1097100 | 891740 | 1537720 | 1257720 | 1918020 | 3232070
BLD16NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total End Uses | 56480 | 301980 | 244620 | 517240 | 205400 | 392460 | 408410 | 805640 | 629390 | 682230 | 1097100 | 891740 | 1537720 | 1257720 | 1918020 | 3232070
BLD16NEW |  |  | Purchased Cooling (MJ)
BLD16NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Purchased Heating (MJ)
BLD16NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total Building (MJ) | 1603280 | 1281310 | 1316300 | 1450190 | 1039860 | 1322270 | 1248100 | 1745670 | 1575370 | 1537740 | 2063120 | 1863870 | 2522940 | 2252360 | 2917490 | 4274220
BLD16NEW |  | Energy - End Use Intensities
BLD16NEW |  |  | Electricity (MJ/m2)
BLD16NEW |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Cooling (elec) | 76.1262 | 14.1858 | 26.2971 | 5.8034 | 0.77764 | 14.3533 | 0.33505 | 4.9492 | 4.4818 | 0.42812 | 3.2347 | 2.85 | 2.5046 | 1.4457 | 0.97205 | 0.19648
BLD16NEW |  |  | Interior Lighting (elec) | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271 | 112.7271
BLD16NEW |  |  | Exterior Lighting (elec) | 29.0396 | 29.0292 | 29.023 | 29.0189 | 28.9961 | 28.9899 | 29.0044 | 28.9878 | 28.9982 | 28.9403 | 28.992 | 28.9754 | 28.9734 | 28.9672 | 28.9506 | 28.7728
BLD16NEW |  |  | Interior Equipment (elec) | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961 | 21.5961
BLD16NEW |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Fans (elec) | 80.4198 | 25.0066 | 31.9991 | 23.807 | 8.4837 | 14.6346 | 9.9997 | 26.1544 | 27.8441 | 13.2427 | 33.2421 | 34.907 | 37.9618 | 40.9751 | 42.4663 | 52.2447
BLD16NEW |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total End Uses | 319.9107 | 202.5426 | 221.6445 | 192.9524 | 172.5827 | 192.303 | 173.6644 | 194.4167 | 195.6473 | 176.9342 | 199.7919 | 201.0556 | 203.7629 | 205.7111 | 206.7121 | 215.5371
BLD16NEW |  |  | Gas (MJ/m2)
BLD16NEW |  |  | Heating (gas) | 11.6812 | 62.4554 | 50.5922 | 106.9754 | 42.4808 | 81.1684 | 84.4672 | 166.6222 | 130.1702 | 141.0986 | 226.9019 | 184.4294 | 318.0307 | 260.1212 | 396.6843 | 668.4557
BLD16NEW |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total End Uses | 11.6812 | 62.4554 | 50.5922 | 106.9754 | 42.4808 | 81.1684 | 84.4672 | 166.6222 | 130.1702 | 141.0986 | 226.9019 | 184.4294 | 318.0307 | 260.1212 | 396.6843 | 668.4557
BLD16NEW |  |  | Purchased Cooling (MJ/m2)
BLD16NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Purchased Heating (MJ/m2)
BLD16NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total Building (MJ/m2) | 331.5898 | 265.0001 | 272.2367 | 299.9278 | 215.0635 | 273.4714 | 258.1316 | 361.0389 | 325.8175 | 318.0349 | 426.6938 | 385.485 | 521.7936 | 465.8324 | 603.3943 | 883.9928
BLD16NEW |  | Peak Energy Demand
BLD16NEW |  |  | Electricity Peak Demand (kW)
BLD16NEW |  |  | Jan | 127.2383 | 67.6128 | 69.4926 | 66.8485 | 70.5303 | 72.3603 | 70.8344 | 75.9973 | 67.7769 | 71.7569 | 78.553 | 79.0982 | 79.9579 | 81.2397 | 81.0135 | 83.6138
BLD16NEW |  |  | Feb | 135.299 | 67.7457 | 69.5169 | 66.8485 | 61.6073 | 63.4373 | 61.9114 | 67.1833 | 67.6755 | 62.8339 | 78.3262 | 70.1752 | 71.0349 | 72.3167 | 72.0905 | 83.6138
BLD16NEW |  |  | Mar | 141.7339 | 67.5584 | 75.087 | 66.7721 | 61.6073 | 63.4373 | 61.9114 | 67.0743 | 67.6755 | 62.8339 | 69.4032 | 70.1752 | 71.0349 | 72.3167 | 72.0905 | 74.6908
BLD16NEW |  |  | Apr | 153.9767 | 71.1271 | 80.095 | 67.4648 | 61.6073 | 66.1814 | 61.9114 | 67.0743 | 67.9068 | 62.8339 | 69.4032 | 69.9709 | 70.7377 | 71.9747 | 72.0905 | 74.6908
BLD16NEW |  |  | May | 173.3455 | 88.4376 | 95.9885 | 75.2994 | 62.0277 | 78.3211 | 62.1702 | 68.1548 | 74.3341 | 63.335 | 73.3444 | 74.3972 | 72.6639 | 72.5573 | 72.1976 | 74.3523
BLD16NEW |  |  | Jun | 177.4184 | 94.6565 | 118.2406 | 85.2637 | 62.567 | 94.1524 | 62.8272 | 86.3867 | 85.9631 | 66.2054 | 87.359 | 84.3753 | 88.7366 | 88.2498 | 79.7732 | 78.0327
BLD16NEW |  |  | Jul | 188.6094 | 101.5503 | 117.5225 | 96.6857 | 68.5909 | 93.7033 | 70.664 | 93.8074 | 90.8411 | 73.1376 | 93.4574 | 91.8588 | 88.8789 | 90.4173 | 89.125 | 81.4513
BLD16NEW |  |  | Aug | 191.3136 | 102.3148 | 118.2138 | 91.7564 | 73.3298 | 93.3477 | 68.6033 | 95.7047 | 92.1517 | 72.2846 | 92.6229 | 94.7958 | 91.3961 | 88.5916 | 87.9027 | 82.485
BLD16NEW |  |  | Sep | 178.715 | 93.8807 | 108.4182 | 83.0667 | 70.4346 | 92.0866 | 74.0355 | 81.8402 | 78.3105 | 69.2129 | 82.1045 | 82.2492 | 80.7948 | 80.7495 | 73.4867 | 74.4954
BLD16NEW |  |  | Oct | 159.2686 | 79.2639 | 84.1919 | 68.5293 | 62.6317 | 70.335 | 62.5392 | 68.4819 | 68.7809 | 63.0327 | 70.1334 | 71.4269 | 71.0866 | 72.5264 | 71.744 | 83.133
BLD16NEW |  |  | Nov | 134.2066 | 68.6891 | 71.8598 | 66.7721 | 70.5303 | 72.3603 | 70.8344 | 75.9973 | 76.5985 | 71.7569 | 78.3262 | 78.8939 | 79.6607 | 80.8977 | 81.0135 | 83.6138
BLD16NEW |  |  | Dec | 123.8079 | 67.5584 | 69.4926 | 66.8485 | 70.5303 | 72.3603 | 70.8344 | 75.9973 | 76.5985 | 71.7569 | 78.3262 | 79.0982 | 79.9579 | 81.2397 | 81.0135 | 83.6138
BLD16NEW |  |  | Time of Peak Electrical Demand
BLD16NEW |  |  | Jan | 25-JAN-13:30 | 11-JAN-09:09 | 02-JAN-09:09 | 02-JAN-09:09 | 02-JAN-16:00 | 02-JAN-16:40 | 02-JAN-16:00 | 02-JAN-16:49 | 04-JAN-09:09 | 02-JAN-16:30 | 06-JAN-16:30 | 05-JAN-16:49 | 02-JAN-16:40 | 03-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
BLD16NEW |  |  | Feb | 24-FEB-13:09 | 21-FEB-15:39 | 28-FEB-15:00 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:39 | 01-FEB-09:09 | 01-FEB-16:00 | 02-FEB-09:09 | 01-FEB-09:09 | 06-FEB-09:09 | 01-FEB-09:09 | 01-FEB-09:09
BLD16NEW |  |  | Mar | 27-MAR-13:30 | 01-MAR-09:09 | 17-MAR-14:00 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09 | 02-MAR-09:09 | 01-MAR-09:09 | 02-MAR-09:09 | 01-MAR-09:09 | 01-MAR-09:09
BLD16NEW |  |  | Apr | 04-APR-13:30 | 17-APR-15:39 | 26-APR-14:00 | 14-APR-15:00 | 03-APR-08:09 | 21-APR-15:39 | 03-APR-08:09 | 03-APR-08:09 | 21-APR-15:00 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09 | 03-APR-08:09
BLD16NEW |  |  | May | 24-MAY-12:39 | 26-MAY-14:00 | 30-MAY-14:00 | 15-MAY-14:00 | 30-MAY-14:00 | 31-MAY-15:00 | 17-MAY-14:30 | 15-MAY-14:00 | 31-MAY-15:00 | 04-MAY-14:00 | 05-MAY-13:00 | 23-MAY-15:00 | 31-MAY-13:20 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:00
BLD16NEW |  |  | Jun | 20-JUN-13:09 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-15:30 | 29-JUN-15:39 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 30-JUN-14:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-15:00
BLD16NEW |  |  | Jul | 10-JUL-13:30 | 31-JUL-14:39 | 11-JUL-15:00 | 03-JUL-15:30 | 10-JUL-15:00 | 24-JUL-15:00 | 03-JUL-13:09 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:39 | 13-JUL-15:39 | 21-JUL-15:00 | 06-JUL-15:30 | 21-JUL-15:00
BLD16NEW |  |  | Aug | 18-AUG-12:00 | 28-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-13:20 | 04-AUG-15:09 | 15-AUG-12:39 | 04-AUG-14:00 | 01-AUG-14:50 | 07-AUG-15:30 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-15:20 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-15:00
BLD16NEW |  |  | Sep | 06-SEP-12:30 | 15-SEP-13:00 | 08-SEP-14:09 | 11-SEP-13:00 | 25-SEP-12:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 01-SEP-14:00 | 01-SEP-15:50 | 05-SEP-13:00 | 06-SEP-14:00 | 14-SEP-14:00 | 01-SEP-15:00 | 07-SEP-14:00 | 07-SEP-15:00
BLD16NEW |  |  | Oct | 06-OCT-13:30 | 13-OCT-13:00 | 02-OCT-14:00 | 12-OCT-15:00 | 05-OCT-13:50 | 03-OCT-15:20 | 13-OCT-14:00 | 03-OCT-14:50 | 13-OCT-14:00 | 17-OCT-14:00 | 31-OCT-13:30 | 05-OCT-14:00 | 06-OCT-14:00 | 06-OCT-15:00 | 02-OCT-08:09 | 23-OCT-08:09
BLD16NEW |  |  | Nov | 07-NOV-13:00 | 01-NOV-14:00 | 13-NOV-15:09 | 01-NOV-08:09 | 06-NOV-16:00 | 06-NOV-16:40 | 10-NOV-16:00 | 06-NOV-16:00 | 13-NOV-16:00 | 06-NOV-16:49 | 06-NOV-16:40 | 06-NOV-16:49 | 06-NOV-16:00 | 08-NOV-16:00 | 24-NOV-16:30 | 01-NOV-08:09
BLD16NEW |  |  | Dec | 14-DEC-13:09 | 01-DEC-09:09 | 01-DEC-09:09 | 22-DEC-09:09 | 01-DEC-16:49 | 01-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 13-DEC-16:30 | 08-DEC-16:40 | 05-DEC-16:19 | 01-DEC-09:09
BLD16NEW |  | Source Energy
BLD16NEW |  |  | Total Source Energy (GJ) | 5192.43 | 3886.67 | 3656.84 | 3703.27 | 2806.94 | 3754.49 | 3044.83 | 4241.3 | 3826.06 | 2235.28 | 4623.55 | 4199.32 | 5065.39 | 4830.79 | 5529.67 | 7251.98
BLD16NEW |  |  | Total Source Energy (MJ/m2) | 1073.9 | 803.84 | 756.31 | 765.91 | 580.53 | 776.5 | 629.73 | 877.18 | 791.3 | 462.3 | 956.24 | 868.5 | 1047.62 | 999.1 | 1143.65 | 1499.85
BLD16NEW |  | Water Consumption (m3)
BLD16NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  | Emissions
BLD16NEW |  |  | Carbon Equivalent (kg) | 118854.8288 | 96185.593 | 94275.858 | 89155.7906 | 30792.6881 | 94188.5279 | 34623.3568 | 84992.2456 | 118691.5983 | 29610.777 | 162848.884 | 126390.2137 | 121405.4286 | 123646.1797 | 129618.5793 | 139740.7041
BLD16NEW |  |  | CO2 (kg) | 275798.9753 | 243426.0182 | 224079.3837 | 208127.0432 | 83023.7778 | 226771.5865 | 94054.0498 | 199992.6242 | 282908.4989 | 76659.7595 | 387249.1216 | 303491.997 | 296075.643 | 300361.1448 | 319013.7512 | 372443.795
BLD16NEW |  |  | NOX (kg) | 483.8826 | 313.5651 | 368.7603 | 374.3218 | 71.6071 | 356.9206 | 81.5976 | 354.0501 | 468.6105 | 98.3316 | 652.9526 | 493.1525 | 466.8225 | 476.3428 | 490.5125 | 408.5163
BLD16NEW |  |  | SO2 (kg) | 1839.1666 | 1297.685 | 1197.1278 | 909.7654 | 674.5479 | 1420.8525 | 678.8328 | 953.4036 | 1147.6426 | 183.8597 | 1808.6901 | 1179.4384 | 646.3228 | 738.06 | 655.7702 | 1474.466
BLD16NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD16NEW |  |  | Hg (kg) | 0.0084 | 0.0037 | 0.0033 | 0.0034 | 0.0003 | 0.0027 | 0.0003 | 0.0039 | 0.0045 | 0.0008 | 0.0056 | 0.0047 | 0.0049 | 0.0053 | 0.005 | 0.0053
BLD16NEW |  |  | Water for Electricity (m3) | 227.6201 | 442.6318 | 8842.64 | 1618.05 | 4069.78 | 7085.66 | 4095.31 | 59.2838 | 1193.2 | 2427.92 | 416.3133 | 1226.19 | 424.5864 | 17501.3 | 430.7296 | 295.7621

## Picture
DOE Commercial Building Benchmark - Warehouse

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 10.1 | 56.3 | 2935.64
| Sat |  |  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.4
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 9.8 | 54.22 | 2827.19
| Sat |  |  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35.2 | 1835.43
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
| Sat |  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  |  |  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  |  |  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CLGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8 | 4485.6 | 233892
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 660 | 3972 | 207111.43
| Sat |  |  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 672
| Sun |  |  |  | Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
|  | HTGSETP_BulkStorage_SCH | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
|  | HTGSETP_FineStorage_SCH | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 432.5 | 2584 | 134737.14
[5 empty] | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
| Sat |  |  |  | Sat | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 421.5
| Sun |  |  |  | Other | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 372
|  | HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
[5 empty] | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MinOA_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 3337.14
[5 empty] | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchGas | WD |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sat |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0